제6장 각 社의 PLC와 연결

1. MT 500

(1) 프린터 (25 Pin D female)

| 1 | STB | OUT | 8 | DATA6 | OUT |
| --- | --- | --- | --- | --- | --- |
| 2 | DATA0 | OUT | 9 | DATA7 | OUT |
| 3 | DATA1 | OUT | 11 | BUSY | IN |
| 4 | DATA2 | OUT | 15 | ERROR | IN |
| 5 | DATA3 | OUT | 16 | INIT | OUT |
| 6 | DATA4 | OUT | 17-25 | ### GND |  |
| 7 | DATA5 | OUT |  |  |  |

(2) PC [RS-232] & PLC [RS485] (9Pin D male형)

PC [RS-232]	  PLC [RS-485]

| 7 | SD(TXD) | OUT |
| --- | --- | --- |
| 8 | RD(RXD) | IN |
| 5 | GND |  |

| 1 | RX- | IN |
| --- | --- | --- |
| 2 | RX+ | IN |
| 3 | TX- | OUT |
| 4 | TX+ | OUT |
| 5 | GND |  |

(3) PLC [RS-232] (9Pin D female형)

PLC [RS-232]

| 2 | SD (TXD) | OUT |
| --- | --- | --- |
| 3 | RD (RXD) | IN |
| 5 | GND |  |
| 7 | CS (CTS) | IN |
| 8 | RS (RTS) | OUT |

(4) MT5-PCCAB	( CABLE 별도로 구매, MT5-PCCAB의 길이는 약2M)

MTS-PCCAB는  ON-Line Simulation 때, CABLE을 이용하여 이미 완성된 MT Data 또는 PC를 이용하여 MT 통신과 PLC연결 CABLE을 이용합니다.

이에 PC에서 MT와 PLC의 작업을 Online-Simulator 합니다. MT와 PLC의 연결은 각 PLC 결선도를 참고 바랍니다.

## PC

## HMI

## PLC

## MT5-PCCAB

## PLC 연결

## PLC

(5) 작화전송 CABLE (MT5-PC)

## PC

## HMI

## MT5-PC

PC					MT500 PLC [RS-232]

9P D-SUB Female			9P D-SUB Female

| 2 | RXD | ←――――――――――→ | 7 | ## TXD |
| --- | --- | --- | --- | --- |
| 3 | TXD | ←――――――――――→ | 8 | RXD |
| 5 | GND | ←――――――――――→ | 5 | GND |
| 7 | ## TXD | ←――――――――――→ | 2 | RXD |
| 8 | RXD | ←――――――――――→ | 3 | TXD |

이 CABLE을 이용하여 미리 작화 된 DATA를 전송합니다.

2.  Mitsubishi FX0n/2

Mitsubishi FX0s/FX0n/FX1s/FX1n/FX2 PLC

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | Mitsubishi FX0n/FX2 | Mitsubishi FX0n/FX2 |  |
| Com port | RS422 | RS232/RS422 |  |
| Baud rate | 9600 | 9600/~/115200 | PLC설정과 일치시킴 |
| Parity bit | Even | Even, Odd, None | PLC설정과 일치시킴 |
| Data Bits | 7 | 7,8 | PLC설정과 일치시킴 |
| Stop Bits | 1 | 1,2 | PLC설정과 일치시킴 |
| HMI Station No. | 0 | 0~255 |  |
| PLC Station No. | 0 | 0~255 | PLC설정과 일치시킴 |

PLC Setting:

| Communication mode | 9600, Even , 7, 1 |
| --- | --- |

Wiring diagram:

MT500 PLC [RS-485]	Mitsubishi FX series PLC CPU			RS422 Port

9P D-SUB Female	8P MiniDin Male

| 1 | RX- |  | 4 | TX- |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | 7 | TX+ |
| 3 | TX- |  | 1 | RX- |
| 4 | TX+ |  | 2 | RX+ 8Pin miniDin Female |
| 5 | GND |  | 3 | ### GND |

3.  Mitsubishi FX2n

Mitsubishi FX2n series PLC

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | Mitsubishi FX2n | Mitsubishi FX2n |  |
| Com port | RS422 | RS232/RS422 |  |
| Baud rate | 9600 | 9600/~/115200 | PLC setting과 일치시킴 |
| Parity bit | Even | Even, Odd, None | PLC setting과 일치시킴 |
| Data Bits | 7 | 7,8 | PLC setting과 일치시킴 |
| Stop Bits | 1 | 1,2 | PLC setting과 일치시킴 |
| HMI Station No. | 0 | 0~255 |  |
| PLC Station No. | 0 | 0~255 | PLC setting과 일치시킴 |

PLC Setting:

| Communication mode | 9600, Even , 7, 1 |
| --- | --- |

Wiring diagram:

MT500 PLC [RS-485]	Mitsubishi FX series PLC CPU

RS422 Port

9P D-SUB Female	8P MiniDin Male

| 1 | RX- |  | 4 | TX- |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | 7 | TX+ |
| 3 | TX- |  | 1 | RX- 8Pin miniDin Female |
| 4 | TX+ |  | 2 | RX+ |
| 5 | GND |  | 3 | GND |

4.  MITSUBISHI FX2n D(bit)

Mitsubishi FX2n series PLC

HMI Setting:

| PLC type | MITSUBISHI FX2n D(bit) |
| --- | --- |
| Com port setting | RS422, 9600, E, 7, 1(refer to PLC) |
| HMI Node number | 0 (none) |
| PLC Node number | 0 (none) |

PLC Setting:

| Communication mode Select | 9600, E, 7, 1(default) |
| --- | --- |

Wiring diagram:

MT500 PLC [RS-485]	Mitsubishi FX series PLC CPU

RS422 Port

9P D-SUB Female	8P MiniDin Male

| 1 | RX- |  | 4 | TX- |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | 7 | TX+ |
| 3 | TX- |  | 1 | RX- 8Pin miniDin Female |
| 4 | TX+ |  | 2 | RX+ |
| 5 | GND |  | 3 | GND |

5.  Mitsubishi FX2N-485-BD, FX2N-232-BD,
 FX1N-485-BD and FX1N-232-BD

Mitsubishi FX0n/FX2/FX2n COM For Communication Module BD
FX2N-485-BD, FX2N-232-BD, FX1N-485-BD and FX1N-232-BD

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | Mitsubishi FX0n/2 / Mitsubishi FX 2n | Mitsubishi FX0n/2 / Mitsubishi FX 2n | PLC CPU기종과 일치시킴 |
| Com port | RS232/RS485 2w/4w | RS232/RS485 2w/4w | BD module에 맞출 것. |
| Baud rate | 9600 | 9600 | PLC setting과 일치시킴 |
| Parity bit | Even | Even | PLC setting과 일치시킴 |
| Data Bits | 7 | 7 | PLC setting과 일치시킴 |
| Stop Bits | 1 | 1 | PLC setting과 일치시킴 |
| HMI Station No. | 0 | 0 |  |
| PLC Station No. | 0 | 0 | PLC setting과 일치시킴 |

PLC Setting:

| Communication mode | D8120의 값이 0으로 되어있어야 BD로 통신가능 |
| --- | --- |

FX2N-485-BD, FX1N-485-BD, FX2N-232-BD, FX1N-232-BD

Wiring diagram:

Communi station Module RS232BD:

MT500 PLC [RS-232]	RS232BD Module

9P D-SUB Male	9P D-SUB Female

| 2 | TXD |  | 2 | RX |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 3 | TX |
| 5 | GND |  | 5 | GND |

Communi station Module RS485BD:

MT500 PLC [RS-485] 	RS485BD Module

9P D-SUB Female	5P terminal

| 1 | RX- |  | SDB |
| --- | --- | --- | --- |
| 2 | RX+ |  | SDA |
| 3 | TX- |  | RDB |
| 4 | TX+ |  | RDA |
| 5 | GND |  | SG |

Communi station Module RS485BD:

MT500 PLC [RS-485] 	RS485BD Module

9P D-SUB Female	5P terminal

| 1 | RX- |  | SDB |
| --- | --- | --- | --- |
| 2 | RX+ |  | SDA |
| 3 | TX- |  | RDB |
| 4 | TX+ |  | RDA |
| 5 | GND |  | SG |

6.  Mitsubishi FX2N-10GM/20GM

Mitsubishi FX2N-10GM, FX2N-20GM.

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | [PDS] FX2N-10GM /20 GM V1.01 |  |  |
| Com port | RS422 4W |  |  |
| Baud rate | 9600 | 9600/~/115200 | PLC setting과 일치시킴 |
| Parity bit | Even | Even, Odd, None | PLC setting과 일치시킴 |
| Data Bits | 8 | 7,8 | PLC setting과 일치시킴 |
| Stop Bits | 1 | 1,2 | PLC setting과 일치시킴 |
| HMI Station No. | 0 |  | 설정 없음. |
| PLC Station No. | 0 |  | 설정 없음. |

PLC Setting:

| Wiring diagram: Communication mode | 9600,Even, 8,1 |
| --- | --- |

MT500 PLC [RS-485]	Mitsubishi

FX2N-10GM/20GM

9P D-SUB Female	8P MiniDin Male

| 1 | RX- |  | 4 | TX- |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | 7 | TX+ |
| 3 | TX- |  | 1 | RX- 8Pin miniDin Female |
| 4 | TX+ |  | 2 | RX+ |
| 5 | GND |  | 3 | GND |

7.  Mitsubishi J2-S100

MITSUBISHI J2-S100(MR-J2-10C)

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | Mitsubishi J2-S100 |  |  |
| Com port | RS485 4W | RS485 4W, RS232 |  |
| Baud rate | 9600 | 9600, 19200 |  |
| Parity bit | Even | Even, Odd, None |  |
| Data Bits | 8 | 8 |  |
| Stop Bits | 1 | 1 |  |
| HMI Station No. | 0 |  |  |
| PLC Station No. | 0 | 0~15 |  |

PLC Setting:

| Wiring diagram: Communication mode |  |
| --- | --- |

RS-485 4W: MT500 PLC [RS-485]	J2-S100

9P D-SUB Female	RS-422

| 1 | RX- |  | 19 | SDN |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | 9 | SDP |
| 3 | TX- |  | 15 | RDN |
| 4 | TX+ |  | 5 | RDP |
| 5 | GND |  | 11 | GND |
|  |  |  | 1 | GND |

RS-232: MT500 PLC [RS-232]	J2-S100

RS-232	9P D-SUB Male

| 2 | TX |  | 2 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RX |  | 12 | TXD |
| 5 | GND |  | 11 | GND |
|  |  |  | 1 | GND |

8.  MITSUBISHI A1S

MITSUBISHI A1S

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | MITSUBISHI A1S |  |  |
| Com port | RS232 |  |  |
| Baud rate | 9600 |  |  |
| Parity bit | Odd |  |  |
| Data Bits | 8 |  |  |
| Stop Bits | 1 |  |  |
| HMI Station No. | 0 |  |  |
| PLC Station No. | 0 |  |  |

PLC Setting:

| Wiring diagram: MT-DRC5 Cable 사용하여 통신함. Communication mode | 9600, Odd, 8, 1 |
| --- | --- |

8-1.  MITSUBISHI AnS CPU

MT500

PLC [RS-232]

MITSUBISHI

RS422/RS232

Converter Cable

MT5_AnS Cable

Mitsubishi	MT5_AnS Cable	MT500

RS-422	PLC [RS232]

DB25 Male	9P D-SUB Female

| 2 | RX+ |  | RD | Yellow | 2 | TD |
| --- | --- | --- | --- | --- | --- | --- |
| 3 | TX+ |  | TD | Red | 3 | RD |
| 4 | DSR+ |  | GND | Purple | 5 | GND |
| 7 | GND |  | RTS | Black | 7 | CTS |
| 15 | RX- |  | CTS | White | 8 | RTS |
| 16 | TX- |  |  |  |  |  |
| 17 | DSR- |  |  |  |  |  |

9.  MITSUBISHI A2A

MITSUBISHI A2A

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | MITSUBISHI A2A |  |  |
| Com port | RS232 |  |  |
| Baud rate | 9600 |  |  |
| Parity bit | Odd |  |  |
| Data Bits | 8 |  |  |
| Stop Bits | 1 |  |  |
| HMI Station No. | 0 |  |  |
| PLC Station No. | 0 |  |  |

PLC Setting:

| Wiring diagram: MT-DRC5 Cable 사용하여 통신함. Communication mode | 9600, Odd, 8, 1 |
| --- | --- |

10.  MITSUBISHI A2US

MITSUBISHI A2US

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | MITSUBISHI A2US |  |  |
| Com port | RS232 |  |  |
| Baud rate | 9600 |  |  |
| Parity bit | Odd |  |  |
| Data Bits | 8 |  |  |
| Stop Bits | 1 |  |  |
| HMI Station No. | 0 |  |  |
| PLC Station No. | 0 |  |  |

PLC Setting:

| Wiring diagram: MT-DRC5 Cable 사용하여 통신함. Communication mode | 9600, Odd, 8, 1 |
| --- | --- |

11.  MITSUBISHI A3N/A1SH

MITSUBISHI A3N/A1SH

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | MITSUBISHI A3N/A1SH |  |  |
| Com port | RS232 |  |  |
| Baud rate | 9600 |  |  |
| Parity bit | Odd |  |  |
| Data Bits | 8 |  |  |
| Stop Bits | 1 |  |  |
| HMI Station No. | 0 |  |  |
| PLC Station No. | 0 |  |  |

PLC Setting:

| Wiring diagram: MT-DRC5 Cable 사용하여 통신함. Communication mode | 9600, Odd, 8, 1 |
| --- | --- |

12.  Mitsubishi AJ71

Mitsubishi A 시리즈 PLC 의 AJ71C24 통신카드

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | MITSUBISHI AJ71 | MITSUBISHI AJ71(AnA/AnU CPU) MITSUBISHI AJ71[format4] pds driver |  |
| Com port | RS485 4W | RS232/RS422 |  |
| Baud rate | 9600 | 9600/19200 |  |
| Parity bit | Even | Even, Odd, None |  |
| Data Bits | 8 | 8 |  |
| Stop Bits | 1 | 1 |  |
| HMI Station No. | 0 |  |  |
| PLC Station No. | 0 |  |  |

PLC Setting:

| Communication mode | Computer Link protocol 9600, Even, 8, 1 (default) |
| --- | --- |
| Mode Setting Switch | Format 1 |
| Parity Check | Enable |
| Sum Check | Enable |

Wiring diagram

RS-485 4W:

MT500 PLC [RS-485]	AJ71C24

9P D-SUB Female	RS-422

| 1 | RX- |  | SDB |
| --- | --- | --- | --- |
| 2 | RX+ |  | SDA |
| 3 | TX- |  | RDB |
| 4 | TX+ |  | RDA |
| 5 | GND |  | GND |

RS-232: A1SJ71UC24-R2

MT500 PLC [232]		RS232 port

9P D-SUB Male		9P D-SUB Male

| 2 | ##### TX+ |  | ##### 2 | ##### RXD |
| --- | --- | --- | --- | --- |
| 3 | RX- |  | 3 | TXD |
| 5 | GND |  | 5 | GND |
|  |  |  | 1 | DCD |
|  |  |  | 4 | DTR |
|  |  |  | 6 | DSR |
|  |  |  | 7 | RTS |
|  |  |  | 8 | CTS |

13. MITSUBISHI AJ71[format4]

Mitsubishi A 시리즈 PLC 의 AJ71C24 통신카드

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | MITSUBISHI AJ71 AJ71 [format4] | MITSUBISHI AJ71 MITSUBISHI AJ71 (AnA/AnU CPU) |  |
| Com port | RS485 4W | RS485 4W, RS232 |  |
| Baud rate | 9600 | 9600/19200 |  |
| Parity bit | Even | Even, Odd, None |  |
| Data Bits | 8 | 8 |  |
| Stop Bits | 1 | 1 |  |
| HMI Station No. | 0 |  |  |
| PLC Station No. | 0 |  |  |

PLC Setting:

| Communication mode | Computer Link protocol 9600, Even, 8, 1 (default) |
| --- | --- |
| Mode Setting Switch | Format 4 (Protocol 4) |
| Parity Check | Enable |
| Sum Check | Enable |

Wiring diagram

RS-485 4W:

MT500 PLC [RS-485]	AJ71C24

9P D-SUB Female	RS-422

| 1 | RX- |  | SDB |
| --- | --- | --- | --- |
| 2 | RX+ |  | SDA |
| 3 | TX- |  | RDB |
| 4 | TX+ |  | RDA |
| 5 | GND |  | GND |

RS-232: A1SJ71UC24-R2

MT500 PLC [232]	RS232 port

9P D-SUB Male	9P D-SUB Male

| 2 | ##### TX+ |  | ##### 2 | ##### RXD |
| --- | --- | --- | --- | --- |
| 3 | RX- |  | 3 | TXD |
| 5 | GND |  | 5 | GND |
|  |  |  | 1 | DCD |
|  |  |  | 4 | DTR |
|  |  |  | 6 | DSR |
|  |  |  | 7 | RTS |
|  |  |  | 8 | CTS |

14.  MITSUBISHI Q00/Q01 CPU

Mitsubishi Q00 and Q01 CPU.

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | MITSUBISHI Melsec_Q [PDS V3.30] |  |  |
| Com port | RS232 |  |  |
| Baud rate | 9600 | 9600/~/115200 |  |
| Parity bit | Odd |  | 고정 |
| Data Bits | 8 |  | 고정 |
| Stop Bits | 1 |  | 고정 |
| HMI Station No. | 0 |  |  |
| PLC Station No. | 0 |  |  |

| PLC Setting: Online Simulator | YES |
| --- | --- |
| Direct Online Simulator | YES |
| Extend address mode | NO |

| Communication mode | use set the PLC Parameter. |
| --- | --- |

1. PLC 프로그램 GX Developer에서 “PLC data list” 
선택->“PLCParameter”

2. “PLC parameter” 선택-> “Serial” 탭.

3. “Use serial communication”체크함.

4. 통신속도설정 9,6Kbps~115,2 Kbps중 선택.

5. “Sum check”선택함.	6. “Transmission wait time”(전송지연시간) 10ms로 설정.

7. “RUN write setting”(런중쓰기가능) 선택함.	8. 확인 버튼을 눌러 창을 닫음.

9. PLC Parameter를 PLC에 쓰기함.	10. PLC 전원 RESET 후 파라메터 적용가능함.

Wiring diagram:

RS-232:

MT500 PLC [232]	Q00/Q01 CPU

RS232 port

9P D-SUB Male	Mini-DIN 6Pin Male

| 2 | TX |  | 1 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RX |  | 2 | MINI-DIN 6PIN Female PLC측 PIN번호 TXD |
| 5 | GND |  | 3 | GND |

* 통신드라이버 (MITSUBISHI Melsec_Q [PDS V3.00])받는 곳:

http://www.enterst.co.kr 사이트 접속 후 자료실/소프트웨어/[이지뷰]-HMI<-->Mitsubishi QJ71 v3.30 통신프로토콜 선택함.

* 다운받은 압축파일을 C:\EB500\V272U\Drivers\에 풀어줌.

15.  MITSUBISHI QJ71

Mitsubishi  Q 시리즈 PLC 의 , QJ71C24 통신카드

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | MITSUBISHI Melsec_Q [PDS V3.00] |  |  |
| Com port | RS232 | RS485 4W, RS232 |  |
| Baud rate | 9600 |  | 고정 |
| Parity bit | Odd |  | 고정 |
| Data Bits | 8 |  | 고정 |
| Stop Bits | 1 |  | 고정 |
| HMI Station No. | 0 |  |  |
| PLC Station No. | 0 |  |  |

| Online Simulator | YES |
| --- | --- |
| Direct Online Simulator | YES |
| Extend address mode | NO |

PLC Setting:

| Communication mode | PLC 기본 Parameter로 설정 없음. |
| --- | --- |

Wiring diagram

RS-485 4W: A1SJ71UC24-R4

MT500 PLC [RS-485]	QJ71C24 CH.2

9P D-SUB Female	RS-422

| 1 | RX- |  | SDB |
| --- | --- | --- | --- |
| 2 | RX+ |  | SDA |
| 3 | TX- |  | RDB |
| 4 | TX+ |  | RDA |
| 5 | GND |  | GND |

RS-232: A1SJ71UC24-R2

MT500 PLC [232]	QJ71C24 CH.1

9P D-SUB Male	9P D-SUB Male

| 2 | ##### TX+ |  | ##### 2 | ##### RXD |
| --- | --- | --- | --- | --- |
| 3 | RX- |  | 3 | TXD |
| 5 | GND |  | 5 | GND |
|  |  |  | 1 | DCD |
|  |  |  | 4 | DTR |
|  |  |  | 6 | DSR |
|  |  |  | 7 | RTS |
|  |  |  | 8 | CTS |

* 통신드라이버 (MITSUBISHI Melsec_Q [PDS V3.00])받는 곳:

http://www.enterst.co.kr 사이트 접속 후 자료실/소프트웨어/[이지뷰]-HMI<-->Mitsubishi QJ71 v3.0 통신프로토콜 선택함.

* 다운받은 압축파일을 C:\EB500\V272U\Drivers\에 풀어줌.

16.  OMRON

OMRON PLC (CPM series, CQM series, C200H/HS/ALPHA series PLC)

HMI Setting:

| Parameters | Recommend |  | Option |  | Notes |  |
| --- | --- | --- | --- | --- | --- | --- |
| PLC type |  | OMRON |  |  |  |  |
| Com port |  | RS232 |  |  |  |  |
| Baud rate |  | 9600 |  | 9600/~/115200 |  | PLC 셋팅과 일치시킴. |
| Parity bit |  | Even |  | Even, Odd, None |  | PLC 셋팅과 일치시킴. |
| Data Bits |  | 7 |  | 7,8 |  | PLC 셋팅과 일치시킴. |
| Stop Bits |  | 2 |  | 1,2 |  | PLC 셋팅과 일치시킴. |
| HMI Station No. |  | 0 |  | 0~255 |  |  |
| PLC Station No. |  | 0 |  | 0~255 |  | PLC 셋팅과 일치시킴. |

| PLC Setting: Communication mode | HOSTLINK protocol |
| --- | --- |

Wiring diagram:

Port (CPM2A, CQM1/1H,C200H/HS/ALPHA series)

MT500 PLC [232]	OMRON PLC CPU port

9P D-SUB Male	9P D-SUB Male

| ##### 2 | ##### TX |  | ##### 3 | ##### RXD |
| --- | --- | --- | --- | --- |
| ##### 3 | ##### RX |  | ##### 2 | ##### TXD |
| ##### 5 | ##### GND |  | ##### 9 | ##### GND |
|  |  |  | ##### 4 | ##### RTS |
|  |  |  | ##### 5 | ##### CTS |

Communication Module:

CPM1-CIF01 Adapter (for CPM1/CPM1A/CPM2A series, CQM1/CQM1H series)

CPM1H-SCB41 communication module (for CQM1H-CPU51/61)

MT500 PLC [232]	Communication Module

RS232 port

9P D-SUB Male	9P D-SUB Male

| ##### 2 | ##### TX |  | ##### 3 | ##### RXD |
| --- | --- | --- | --- | --- |
| ##### 3 | ##### RX |  | ##### 2 | ##### TXD |
| ##### 5 | ##### GND |  | ##### 9 | ##### GND |
|  |  |  | ##### 4 | ##### RTS |
|  |  |  | ##### 5 | ##### CTS |

C200h-LK201, 3G2A6-LK201 Communication module

MT500 PLC [232]	LK201 Adapter

RS232 port

9P D-SUB Male	25P D-SUB Male

| 2 | TX |  | 3 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RX |  | 2 | TXD |
| 5 | GND |  | 7 | GND |
|  |  |  | 4 | RTS |
|  |  |  | 5 | CTS |

C200HW-COM02/03/04/05/06 Communication module

MT500 PLC [232]	Communication Module

RS232 port

9P D-SUB Male	9P D-SUB Male

| 2 | TX |  | 3 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RX |  | 2 | TXD |
| 5 | GND |  | 7 | GND |
|  |  |  | 4 | RTS |
|  |  |  | 5 | CTS |

17.  OMRON (485 2W)

OMRON PLC (CPM series, CQM series,C200H/HS/ALPHA series PLC)

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | OMRON |  |  |
| Com port | RS485 (2W) |  | RS485 2선 모드 |
| Baud rate | 9600 | 9600/~/115200 | PLC 셋팅과 일치시킴. |
| Parity bit | Even | Even, Odd, None | PLC 셋팅과 일치시킴. |
| Data Bits | 7 | 7,8 | PLC 셋팅과 일치시킴. |
| Stop Bits | 2 | 1,2 | PLC 셋팅과 일치시킴. |
| HMI Station No. | 0 | 0~255 |  |
| PLC Station No. | 0 | 0~255 | PLC 셋팅과 일치시킴. |

| PLC Setting: Communication mode | HOSTLINK protocol |
| --- | --- |

Wiring diagram:

Communication Module:

CPM1/CPM1A/CPM2A 시리즈, CQM1/CQM1H 시리즈용 {CPM1-CIF11(RS422) Adapter}
, CQM1H-CPU51/61용 통신카드{CPM1H-SCB41(RS422/485) 통신카드}

MT500 PLC [232]	Communication Module

RS422/485 port

9P D-SUB Male	6P terminal

| 1 | TX |  | SDB |
| --- | --- | --- | --- |
| 2 | ## RX |  | SDA |
| 3 | TX- |  | RDB |
| 4 | TX+ |  | RDA |
| 5 | GND |  | SG |

C200h-LK202,3G2A6-LK202 통신카드

MT500 PLC [232]	LK201 Adapter

RS485 port

9P D-SUB Male	25P D-SUB Male

| 1 | TX |  | SDB |
| --- | --- | --- | --- |
| 2 | ## RX |  | SDA |
| 5 | GND |  | SG |
| 3 | TX- |  | RDB |
| 4 | TX+ |  | RDA |

C200HW-COM03/06 통신카드

MT500 PLC [232]	Communication Module

RS485 port				9P D-SUB Male	9P D-SUB Male

| 1 | TX |  | SDB |
| --- | --- | --- | --- |
| 2 | ## RX |  | SDA |
| 5 | GND |  | SG |
| 3 | TX- |  | RDB |
| 4 | TX+ |  | RDA |

18.  OMRON CQM1H-CPU61

OMRON CPM1H, CQM1H, C200H, C200HS and ALPHA. (Host Link Protocol),

확장 어드레스 모드

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | [pds]OMRON CQM1H-CPU61 |  |  |
| Com port | RS232 | RS232, RS422, RS485 |  |
| Baud rate | 9600 | 9600, 19200 |  |
| Parity bit | Even | Even, Odd, None |  |
| Data Bits | 7 | 7 or 8 |  |
| Stop Bits | 2 | 1 or 2 |  |
| HMI Station No. | 0 |  |  |
| PLC Station No. | 0 | 0-255 |  |

| PLC Setting: Communication mode | HOSTLINK protocol |
| --- | --- |

Wiring diagram:

RS-232: MT500 PLC [232]	OMRON CPU

9P D-SUB Male	RS-232 9P D-SUB Male

| 2 | TX |  | 3 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RX |  | 2 | TXD |
| 5 | GND |  | 9 | GND |
|  |  |  | 4 | RTS |
|  |  |  | 5 | CTS |

RS-485: CQM1H-SCB41, CPM1H-SCB41

MT500 PLC [RS-485]	OMRON

9P D-SUB Male	Station 1

| 1 | RX- |  | 1 | SDB |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | 2 | SDA |
|  |  |  | Station 2 |  |
|  |  |  | 1 | SDB |
|  |  |  | 2 | SDA |

18-1.  확장 어드레스 모드 사용하기.

MT500 과 다국 PLC 간의 RS485 통신.

Station No. 1

Station No. 2

PLC 타입과 통신상태     설정함

Extended Address Mode
로 선택함

어드레스 형식 설정은:
'#'앞에 스테이션 입력, 번호 형식은 (0~255)중 선택, '#' 뒤에는 설정 스테이션의 I/O, 데이터 레지스터. 예)

IR: 1#010 스테이션1번 PLC의 IR010

DM: 0#1 스테이션0번 PLC의 DM1

19.  KOYO

KOYO Direct Logic series PLC DL05, DL105, DL205, DL305 and DL405 series

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | KOYO DIRECT |  |  |
| Com port | RS232 | RS232, RS485 |  |
| Baud rate | 9600 | 9600, 19200, 38400 |  |
| Parity bit | Odd | Even, Odd, None |  |
| Data Bits | 8 | 7, 8 |  |
| Stop Bits | 1 | 1 |  |
| HMI Station No. | 0 |  |  |
| PLC Station No. | 1 | 1-90 |  |

PLC Setting:

|  | 1. The PLC must not have a password. 2. PLC must be set for Full Duplex operation. 3. PLC must be set for No Hardware Handshaking. 4. The PLC must be set to use the ‘K’ Sequence Protocol. 5. Set the mode switch to the TERM mode 6. When using the D4-440 CPU, you must set the station number to 1. |
| --- | --- |

Wiring diagram:

1) CPU unit: DL05/DL105/DL230/DL240/DL250/DL350/DL450 RS232 port

MT500 PLC [232]	KOYO Direct Logic PLC

9P D-SUB Male	RS232 port

6P RJ12 phone jack

| 2 | TXD |  | 3 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 4 | TXD |
| 5 | GND |  | 1 | GND |

2) CPU unit: DL250 CPU Port2 RS232

MT500 PLC [RS-485]	KOYO Direct Logic PLC

9P D-SUB Female	DL250 CPU RS232 Port2

15P D-SUB Male

| 2 | TXD |  | 3 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 2 | TXD |
| 5 | GND |  | 7 | GND 15P D-SUB Female |
|  |  |  | 4 | RTS |
|  |  |  | 5 | CTS |

3) CPU unit: DL250 CPU Port2 RS422

MT500 PLC [RS-485]	KOYO Direct Logic PLC

DL250 CPU RS422 Port2

9P D-SUB Female 	15P D-SUB Male

| 1 | RX- |  | 10 | TX- |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | 9 | TX+ |
| 3 | TX- |  | 6 | RX- 15P D-SUB Female |
| 4 | TX+ |  | 13 | RX+ |
| 5 | GND |  | 7 | GND |
|  |  |  | 11 | RTS+ |
|  |  |  | 14 | CTS+ |
|  |  |  | 12 | RTS- |
|  |  |  | 15 | CTS- |

Note: DL250 CPU Port2 include RS232 and RS422

4) CPU unit: DL430/DL440/DL450 CPU unit Port0 RS232

MT500 PLC [232]	KOYO Direct Logic PLC

DL405 CPU RS232 Port0

9P D-SUB Male	15P D-SUB Male

| 2 | TXD |  | 3 | RX |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 2 | TX |
| 5 | GND |  | 13 | GND |
|  |  |  | 1 | YOP |
|  |  |  | 7 | CTS |
|  |  |  | 2 | YOM |
|  |  |  | 4 | ONLINE |
|  |  |  | 14 | GND |

5) CPU unit: DL430/DL440/DL450 CPU unit Port1 & DL350 CPU unit Port2 RS232

MT500 PLC [232]	KOYO Direct Logic PLC

DL305/405 CPU RS232 Port

9P D-SUB Male	25P D-SUB Male

| 2 | TX |  | 3 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RX |  | 2 | TXD |
| 5 | GND |  | 7 | GND |
|  |  |  | 4 | RTS |
|  |  |  | 5 | CTS |

6) CPU unit: DL430/DL440/DL450 CPU unit Port1 & DL350 CPU unit Port2 RS422

MT500 PLC [RS-485]	KOYO Direct Logic PLC

DL305/405 CPU RS422 Port

9P D-SUB Female	25P D-SUB Male

| 1 | RX- |  | 16 | TX- |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | 14 | TX+ |
| 3 | TX- |  | 10 | RX- |
| 4 | TX+ |  | 9 | RX+ |
| 5 | GND |  | 7 | GND |
|  |  |  | 19 | RTS+ |
|  |  |  | 11 | CTS+ |
|  |  |  | 18 | RTS- |
|  |  |  | 23 | CTS- |

7) CPU unit: DL450 CPU unit Port3 RS422

MT500 PLC [RS-485]	KOYO Direct Logic PLC

DL405 CPU RS422 Port3

9P D-SUB Female	25P D-SUB Male

| 1 | RX- |  | 13 | TX- |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | 12 | TX+ |
| 3 | TX- |  | 25 | RX- |
| 4 | TX+ |  | 24 | RX+ |
| 5 | GND |  | 7 | GND |

8) Communication unit: DL205 series D2-DCM and DL405 series D4-DCM RS232

MT500 PLC [232]	KOYO Direct Logic PLC

DL205/405 DCM RS232 Port

9P D-SUB Male	25P D-SUB Male

| 2 | TXD |  | 3 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 2 | TXD |
| 5 | GND |  | 7 | GND |
|  |  |  | 4 | RTS |
|  |  |  | 5 | CTS |

# 20.  AB DF1

Micro Logix 1000, 1200, 1500, SLC 5/03, 5/04, 5/05

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | AB DF1 |  |  |
| Com port | RS232 |  |  |
| Baud rate | 19200 | 9600, 19200 |  |
| Parity bit | None | Even, Odd, None |  |
| Data Bits | 8 | 8 |  |
| Stop Bits | 1 | 1 |  |
| HMI Station No. | 0 |  |  |
| PLC Station No. | 1 | 1-31 |  |

PLC Setting:

| Wiring diagram: Communication mode | DF1 Full Duplex protocol 19200, None, 8, 1 (default) |
| --- | --- |

RS-232: Micro Logix 1000,1200, 1500

MT500 PLC [232]	Micro Logix RS232

9P D-SUB Male	8p mini DIN Male

| 2 | TXD |  | 4 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 7 | TXD 8Pin miniDin Female |
| 5 | GND |  | 8 | GND |

RS-232: SLC5/03,04,05 CH0

MT500 PLC [232]	AB CPU CH0 RS-232

9P D-SUB Male	9P D-SUB Male

| 2 | TXD |  | 2 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 3 | TXD |
| 5 | GND |  | 5 | GND |

21. AB Logix pds driver V2.0

Allen-Bradley CompactLogix:

1769-L20, 1769-L30, 1769-L31, 1769-L32E, 1769-L35E

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | AB Logix DF1 |  |  |
| Com port | RS232 |  |  |
| Baud rate | 19200 | 9600, 19200 |  |
| Parity bit | None | Even, Odd, None |  |
| Data Bits | 8 | 8 |  |
| Stop Bits | 1 | 1 |  |
| HMI Station No. | 0 |  |  |
| PLC Station No. | 1 | 1-31 |  |

PLC Setting:

| Communication mode | DF1 Full Duplex protocol 19200, None, 8, 1 (default) Error Check: CRC, Station Address: 1 |
| --- | --- |

Wiring diagram:

RS-232: CompactLogix CPU CH0, CH1 (RS232 DF1)

MT500 PLC [232]	AB CPU CH0 RS-232

9P D-SUB Male	9P D-SUB Male

| 2 | TXD |  | 2 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 3 | TXD |
| 5 | GND |  | 5 | GND |

22.  AB DH485

MicroLogix 1000, 1200, 1500, SLC 5/01, 5/02, 5/03, 5/04, 5/05

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | AB DH485 |  |  |
| Com port | RS485 | RS485, RS232 |  |
| Baud rate | 19200 | 9600, 19200 |  |
| Parity bit | Even | Even, Odd, None |  |
| Data Bits | 8 | 8 |  |
| Stop Bits | 1 | 1 |  |
| HMI Station No. | 0 | 0-31 |  |
| PLC Station No. | 1 | 1-31 |  |

PLC Setting:

| Communication mode | DH485 protocol 19200, Even, 8, 1 (default) |
| --- | --- |
|  | MicroLogix 1000, 1200, 1500, SLC 5/03, 5/04, 5/05 CH0 must set DH485 protocol in channel config. |

Wiring diagram:

RS-485: SLC500 Fixed type, SLC5/01,02,03 CH1.

MT500 can’t connect to 1747-AIC PERIPHERAL PORT

MT500 PLC [RS-485]	AB SLC500 DH485

9P D-SUB Female	RJ8 clip style ports

| 1 | RX- |  | 2 | SDB |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | 1 | SDA RJ8 connector |
| 5 | GND |  | 7 | GND |

RS-232: MicroLogix 1000,1200, 1500 must set DH485 protocol.

MT500 PLC [232]	MicroLogix RS232

9P D-SUB Male	8p mini DIN Male

| 2 | TXD |  | 4 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 7 | TXD 8Pin miniDin Female |
| 5 | GND |  | 8 | GND |

RS-232: SLC5/03,04,05 CH0

MT500 PLC [232]	AB CPU CH0 RS-232

9P D-SUB Male	9P D-SUB Male

| 2 | TXD |  | 2 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 3 | TXD |
| 5 | GND |  | 5 | GND |

23.  AB PLC5

Allen-Bradley PLC-5 Family PLCs using the DF1 Full Duplex protocol.

For the PLC-5/10, PLC-5/15 and PLC-5/25 the MT500 should be connected to:

- The DF1 port on the 1785-KE module;

For the PLC-5/11, PLC-5/20, PLC-5/30 and PLC-5/40 the MT500 should be connected to the Channel 0 Port on the PLC.

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | AB PLC5 |  |  |
| Com port | RS232 |  |  |
| Baud rate | 19200 | 9600, 19200 |  |
| Parity bit | None | Even, Odd, None |  |
| Data Bits | 8 | 8 |  |
| Stop Bits | 1 | 1 |  |
| HMI Station No. | 0 |  |  |
| PLC Station No. | 1 | 1-31 |  |

PLC Setting:

| Wiring diagram: Communication mode | DF1 Full Duplex protocol 19200, None, 8, 1 (default) |
| --- | --- |

RS-232: PLC5 CPU CH0

MT500 PLC [232]	AB CPU CH0 RS-232

9P D-SUB Male	25P D-SUB Male

| 2 | TXD |  | 3 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 2 | TXD |
| 5 | GND |  | 5 | GND |

24.  MODBUS RTU

MODBUS RTU CONTROLLER

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | Modbus RTU |  |  |
| Com port | RS232 | RS232/RS485 | 콘트롤러셋팅과 일치시킴. |
| Baud rate | 9600 | 9600/~/115200 | 콘트롤러셋팅과 일치시킴. |
| Parity bit | Even | Even, Odd, None | 콘트롤러셋팅과 일치시킴. |
| Data Bits | 8 | 7,8 | 콘트롤러셋팅과 일치시킴. |
| Stop Bits | 1 | 1,2 | 콘트롤러셋팅과 일치시킴. |
| HMI Station No. | 0 | 0~255 |  |
| PLC Station No. | 0 | 0~31 | 콘트롤러셋팅과 일치시킴. |

| PLC Setting: Communication mode | Modbus RTU protocol |
| --- | --- |

Wiring diagram:

MODBUS RS232 PORT

MT500 PLC [232]	Modbus RTUControler

9P D-SUB Male	RS232 Port

| 2 | TXD |  | RXD |
| --- | --- | --- | --- |
| 3 | RXD |  | TXD |
| 5 | GND |  | GND |
|  |  |  | RTS |
|  |  |  | CTS |

MODBUS RS422/485 PORT

MT500 PLC [RS-485] 	Modbus RTUControler

9P D-SUB Female	RS422/485 Port

| 1 | RX- |  | TX- |
| --- | --- | --- | --- |
| 2 | RX+ |  | TX+ |
| 3 | TX- |  | RX- |
| 4 | TX+ |  | RX+ |
| 5 | GND |  | GND |

25.  Modbus RTU Server (Modbus RTU Slave)

Modbus RTU Extend support Extend Addressing mode.

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | Modbus RTU Server |  |  |
| Com port | RS232 | RS232, RS485 |  |
| Baud rate | 9600 | 9600/~/115200 |  |
| Parity bit | Even | Even, Odd, None |  |
| Data Bits | 8 | 8 |  |
| Stop Bits | 1 | 1 |  |
| HMI Station No. | 0 |  |  |
| PLC Station No. | 1 | 1~31 | Modbus station No. |

PLC Setting:

| Communication mode | Modbus RTU protocol |
| --- | --- |

LB0 = 0x0001, LB1 = 0x0002, LW0 = 3x0001, LW1 = 3x0002 
Modbus RTU Server doesn’t support function Code 06(to preset single register),
 please use function code, 16(0x10, preset multiple register).

Wiring diagram:

RS232

MT500 PLC [232]	Modbus RTU RS232

9P D-SUB Male	9P D-SUB

| 2 | TXD |  | 3 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 2 | TXD |
| 5 | GND |  | 5 | GND |

RS485 2W

MT500 PLC [RS-485]	Modbus RTU RS485

9P D-SUB Female	9P D-SUB

| 1 | RX- |  | 1 | RX- |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | 2 | RX+ |
| 5 | GND |  | 5 | GND |

26. Modbus RTU TCP/IP

MT500 must have Ethernet port, Modbus RTU TCP/IP device.

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | MODBUS RTU TCP/IP |  |  |
| Com port | Ethernet |  |  |
| HMI Station No. | 0 | Does not apply |  |
| PLC Station No. | 0 | 0~31 | Device ID |

PLC Setting:

| Communication mode |  |
| --- | --- |

Wiring diagram:

RJ45 connector

Ethernet: MT500 to HUB or Switch

MT500 Ethernet		Wire color		   	Ethernet Hub or Switch

RJ45								   RJ45

| 1 | ## TX+ | White/Orange |  | 1 | RX+ |
| --- | --- | --- | --- | --- | --- |
| 2 | TX- | Orange |  | 2 | RX- |
| 3 | RX+ | White/Green |  | 3 | TX+ |
| 4 | BD4+ | Blue |  | 4 | BD4+ |
| 5 | BD4- | White/Blue |  | 5 | BD4- |
| 6 | RX- | Green |  | 6 | TX- |
| 7 | BD3+ | White/Brown |  | 7 | BD3+ |
| 8 | BD3- | Brown |  | 8 | BD3- |

MT500

192.168.10.182

Internet or

Intranet

Modbus RTU TCP/IP Device

210.66.120.180

Router

192.168.10.1

Ethernet: MT500 to HUB or Switch

MT500 Ethernet		Wire color			Modbus TCP Device

RJ45							   RJ45

| 1 | ## TX+ | White/Orange |  | 3 | RX+ |
| --- | --- | --- | --- | --- | --- |
| 2 | TX- | Orange |  | 6 | RX- |
| 3 | RX+ | White/Green |  | 1 | TX+ |
| 4 | BD4+ | Blue |  | 4 | BD4+ |
| 5 | BD4- | White/Blue |  | 5 | BD4- |
| 6 | RX- | Green |  | 2 | TX- |
| 7 | BD3+ | White/Brown |  | 7 | BD3+ |
| 8 | BD3- | Brown |  | 8 | BD3- |

MT500

192.168.10.182

Ethernet

Modbus RTU TCP/IP Device

210.66.120.181

PC Simulator

Ethernet

Computer

Modbus RTU TCP/IP Device

192.168.1.181

192.168.1.10

Use Direct Online Simulator (10 min. time limit) connects to Modbus RTU TCP/IP

Device. The Simulator will use PC’s IP and ignore Local IP address.

MT500 Modbus TCP/IP function code.

| Address type | Read code | Write code |
| --- | --- | --- |
| 0x | 0x01 Read coil | 0x05 write single coil |
| 1x | 0x02 Read discrete input | N/A for write operation |
| 3x | 0x04 Read input register | N/A for write operation |
| 4x | 0x03 Read holding register | 0x10 write multiple register |
| 3x_bit | is equivalent to 3x |  |
| 4x_bit | is equivalent to 4x |  |

27. Modbus RTU Extend

Modbus RTU Extend support Extend Addressing mode.

HMI Setting:

| PLC type | Modbus RTU Extend V3 |
| --- | --- |
| Com port setting | RS232/RS485 (4W)/RS485 (2W),(refer to PLC) |
| HMI Node number | 0 (no use) |
| PLC Node number | 1 (refer to PLC) |
| Parameter 2 | 0 to 1000 Not work for simulation mode HMI will delay (#+1) millisecond before sending command to PLC. Some slow PLC have to setting this parameter |

PLC Setting:

| Communication mode | 9600,E, 8, 1(default) |
| --- | --- |

Wiring diagram:

RS232:	MT500 PLC [232]	Modbus RTU Slave

9P D-SUB Male	RS232

| 2 | TXD |  | #### RXD |
| --- | --- | --- | --- |
| 3 | RXD |  | TXD |
| 5 | GND |  | GND |

RS422:	MT500 PLC [RS-485]	Modbus RTU Slave

9P D-SUB Female	RS422

| 1 | #### RX- |  | TX- |
| --- | --- | --- | --- |
| 2 | RX+ |  | TX+ |
| 3 | TX- |  | RX- |
| 4 | TX+ |  | RX+ |
| 5 | GND |  | GND |

RS485:	MT500 PLC [RS-485]	Modbus RTU Slave

9P D-SUB Female	RS-485

| 1 | RX- |  | RX- |
| --- | --- | --- | --- |
| 2 | RX+ |  | TX+ |
| 5 | GND |  | GND |

28.  Modicon Twido

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | Modbus RTU | Modbus RTU Ext.pds Modbus RTU (485 2w) Modbus RTU (RS232) | The pds driver support Extended Address mode. |
| Com port | RS485 | RS232/RS485 | PLC설정과 일치시킴. |
| Baud rate | 19200 | 19200 | PLC설정과 일치시킴. |
| Parity bit | None | Even, Odd, None | PLC설정과 일치시킴. |
| Data Bits | 8 | 8 | Must set 8 for RTU mode |
| Stop Bits | 1 | 1 | Must set 1 for RTU mode |
| HMI Station No. | 0 | 0~255 |  |
| PLC Station No. | 1 | 0~247 | PLC설정과 일치시킴. |

| PLC Setting: Communication mode Select | 19200, None, 8, 1 Modbus RTU Slave |
| --- | --- |

Wiring diagram:

MT500 PLC [RS-485]	Port1 RS485 port

9P D-SUB Female	8Pin miniDin

| 1 | RX- |  | 2 | B (-) |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | 1 | A (+) |
| 5 | GND |  | 7 | GND 8Pin miniDin Female |
|  |  |  | 5 | DPT |

MT500 PLC [RS-485]	Port2 RS485 port

9P D-SUB Female	3Pin Terminal

| 1 | RX- |  | B (-) |
| --- | --- | --- | --- |
| 2 | RX+ |  | A (+) |
| 5 | GND |  | GND |

MT500 PLC [232]	Port2 RS232

9P D-SUB Male	9P D-SUB Female

| 2 | TXD |  | 2 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 3 | TXD |
| 5 | GND |  | 5 | GND |

29. GE Fanuc SNP-X

GE Fanuc 90 & VersaMax series PLC

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | GE Fanuc SNP-X |  |  |
| Com port | RS485 | RS232/RS485 |  |
| Baud rate | 19200 | 9600/~/115200 | PLC설정과 일치시킴 |
| Parity bit | Odd | Even, Odd, None | PLC설정과 일치시킴 |
| Data Bits | 8 | 7, 8 |  |
| Stop Bits | 1 | 1, 2 | PLC설정과 일치시킴 |
| HMI Station No. | 0 | 0~255 |  |
| PLC Station No. | 0 | 0~255 |  |

PLC Setting:

RJ45 connector

Refer to related PLC manual

Wiring diagram:

CPU port(90-30/VersaMax)

MT500 PLC [485]	90-30/VersaMax

RS485 port

9P D-SUB Female	15P D-SUB Male

| 1 | ## RX- |  | 12 | SDB |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | 13 | SDA |
| 3 | TX- |  | 10 | RDB |
| 4 | TX+ |  | 11 | RDA |
| 5 | GND |  | 7 | GND |
|  |  |  | 9 | RT |
|  |  |  | 6 | RTSA |
|  |  |  | 15 | CTSA |
|  |  |  | 8 | RTSB |
|  |  |  | 14 | CTSB |

CPU port(90-30 series CPU351/352/363/364)

MT500 PLC [232]	90-30/90-70 series

RS232 port

9P D-SUB Male	6P RJ-11 Male

| 2 | TXD |  | 5 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 2 | TXD |
| 5 | GND |  | 3 | GND 6P RJ-11 Male |

CPU port(VersaMax series CPU001/002/005/E05)

MT500 PLC [232]	VersaMax series

RS232 port

9P D-SUB Female	9P SUB-D Female

| 2 | TXD |  | 3 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 2 | TXD |
| 5 | GND |  | 5 | GND |

30.  IDEC

IDEC Micro3, Micro3C, Micro Smart, Open Net Controller series

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | IDEC Micro |  | Support Extend address mode |
| Com port | RS232 | RS232, RS485 | PLC설정과 일치시킴 |
| Baud rate | 9600 | 9600, 19200 | PLC설정과 일치시킴 |
| Parity bit | Even | Even, Odd, None | PLC설정과 일치시킴 |
| Data Bits | 7 | 7, 8 | PLC설정과 일치시킴 |
| Stop Bits | 1 | 1 | PLC설정과 일치시킴 |
| HMI Station No. | 0 |  |  |
| PLC Station No. | 255 (1:1연결 시) | 0~255 | PLC설정과 일치시킴 |

| Online Simulator | YES |
| --- | --- |
| Direct Online Simulator | YES |
| Extend address mode | YES ( PLC 스테이션 번호가 255이면 안됨 ) |

PLC Setting:

| Online Simulator | 9600, E, 7, 1(default), Use Computer Link Protocol |
| --- | --- |

Wiring diagram:

RS232: Micro3C, Micro Smart, Open Net Controller CPU Ladder Port

MT500 PLC [232]	CPU port 1 or port2 RS-232

9P D-SUB Male	8P mini DIN Male

| 2 | TXD |  | 4 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 3 | TXD 8Pin mini DIN Female Pin Layout |
| 5 | GND |  | 7 | GND |

MicroSmart

MT500

MT500

RS485: Micro3 CPU Port, Micro Smart with FC4A-PC2 RS485 Communication Adapter

MT500 PLC [RS-485]	CPU Port RS-485

9P D-SUB Female	8P mini DIN Male

| 1 | RX- |  | 2 | RX- |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | 1 | RX+ 8Pin mini DIN Female Pin Layout |
| 5 | GND |  | 7 | GND |

RS485: Micro3C, Open Net Controller Data Link Terminals,

Micro Smart with FC4A-PC3 RS485 Communication Adapter

MT500 PLC [RS-485]	Data Link Terminals

9P D-SUB Female

| 1 | RX- |  | A | RX- |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | B | RX+ |
| 5 | GND |  | SG | GND |

31.  IDEC Micro

IDEC Micro3, Micro3C, Open Net

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | IDEC Micro |  |  |
| Com port | RS485 | RS232/RS485 |  |
| Baud rate | 9600 | 9600, 19200 |  |
| Parity bit | Even |  |  |
| Data Bits | 7 |  |  |
| Stop Bits | 1 |  |  |
| HMI Station No. | 0 |  |  |
| PLC Station No. | 255 | 0~255 |  |

| Communication mode Select | Micro3C select Loader Protocol |
| --- | --- |

PLC Setting:

| Online Simulator | 9600, E, 7, 1(default), Use Computer Link Protocol |
| --- | --- |

Wiring diagram:

1) Micro3 CPU port

MT500 PLC [RS-485]	Micro3 CPU RS485

9P D-SUB Female	8p mini DIN

8Pin mini DIN
Female 
Pin Layout

| 1 | RX- |  | 2 | RX- |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | 1 | RX+ |
| 5 | GND |  | 7 | GND |

2) Micro3C CPU port

Loader port: Set the protocol selector switch to 0, 2 or 4 to select loader protocol 
for the loader port.

MT500 PLC [232]	Micro3C CPU Loader port

9P D-SUB Male	RS232 8p mini DIN

8Pin mini DIN
Female 
Pin Layout

| 2 | TXD |  | 4 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 3 | TXD |
| 5 | GND |  | 7 | GND |

Data Link Terminals: Set the protocol selector switch to 2, 3 or 4 to select loader protocol for the Data Link Terminal.

MT500 PLC [RS-485]	Micro3C CPU RS485

9P D-SUB Female	DataLink Terminals

| 1 | RX- |  | B |
| --- | --- | --- | --- |
| 2 | RX+ |  | A |
| 5 | GND |  | SG |

Communication Protocols for Loader Port and Data Link Terminals

| Protocol Selector Switch Position | Loader Port Protocol | Data Link Terminal Protocol | Remarks |
| --- | --- | --- | --- |
| 0 | Loader protocol | Data link protocol |  |
| 1 | User protocol | Data link protocol |  |
| 2 | Loader protocol | Loader protocol |  |
| 3 | User protocol | Loader protocol |  |
| 4 | Loader protocol | Loader protocol | Fixed 9600, E, 7, 1 |
| 5~7 | Reserved | Reserved |  |

3) Open Net series CPU port

RS232 Port1 or Port2:

MT500 PLC [232]	Open Net CPU RS232 port

9P D-SUB Male	8p mini DIN

8Pin mini DIN
Female 
Pin Layout

| 2 | TXD |  | 4 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 3 | TXD |
| 5 | GND |  | 7 | GND |

RS485 Terminals:

MT500 PLC [RS-485]	Open Net CPU

9P D-SUB Female	RS485 Terminals

| 1 | RX- |  | ### B |
| --- | --- | --- | --- |
| 2 | RX+ |  | A |
| 5 | GND |  | SG |

Dipswitch

To enable the maintenance mode for the RS485, set the Dipswitch 1 to OFF.

To enable the maintenance mode for the RS232C port 1, set the Dipswitch 2 to OFF.

To enable the maintenance mode for the RS232C port 2, set the Dipswitch 3 to OFF.

# 32.  FACON FB

FACON FBs series, FB MC series, FB MA series need FB-DTBR converter.

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | FACON FB |  |  |
| Com port | RS232 | RS232/RS485 | PLC의 port 셋팅과 일치시킴. |
| Baud rate | 9600 |  | PLC의 port 셋팅과 일치시킴. |
| Parity bit | Even |  | PLC의 port 셋팅과 일치시킴. |
| Data Bits | 7 |  |  |
| Stop Bits | 1 |  |  |
| HMI Station No. | 0 |  |  |
| PLC Station No. | 1 | 0~255 | PLC의 port 셋팅과 일치시킴. |

PLC Setting:

| Communication mode Select |  |
| --- | --- |

Wiring diagram:

1) RS232: CPU port

MT500 PLC [232]	FB CPU port

9P D-SUB Male	15P D-SUB Male

| 2 | TXD |  | 1 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 2 | TXD |
| 5 | GND |  | 6 | GND |
|  |  |  | 3 | RTS |
|  |  |  | 4 | CTS |

2) RS485: CPU port

MT500 PLC [RS-485]	FB CPU port

9P D-SUB Female	15P D-SUB Male

| 1 | RX- |  | 7 | D- |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | 5 | D+ |

3) RS232: FB-DTBR/DTBR-E

MT500 PLC [232]	FB-DTBR/DTBR-E

9P D-SUB Male	15P D-SUB Male

| 2 | TXD |  | 1 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 2 | TXD |
| 5 | GND |  | 6 | GND |
|  |  |  | 3 | RTS |
|  |  |  | 4 | CTS |

4) RS485: FB-DTBR/DTBR-E

MT500 PLC [232]	FB-DTBR/DTBR-E

9P D-SUB Male	9P D-SUB Male

| 2 | TXD |  | 3 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 2 | TXD |
| 5 | GND |  | 5 | GND |

5) RS485: FB-DTBR/DTBR-E

MT500 PLC [RS-485]	FB-DTBR/DTBR-E

9P D-SUB Female	3P Terminal Block

| 1 | RX- |  |  | D- |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  |  | D+ |

6) RS232: FBs Port0

MT500 PLC [232]	FB-DTBR/DTBR-E

9P D-SUB Male	4P Mini-Din Male

| 2 | TXD |  | 4 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 3 | TXD 4P Mini-Din Female |
| 5 | GND |  | 2 | GND |

33.  TELEMECANIQUE UniTelWay TSZ37/ TSX07

Modicon TSX Micro & Nano & Neza series PLC

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | Telemecanique UniTelWay |  |  |
| Com port | RS485 | RS232/RS485 | PLC설정과 일치시킴. |
| Baud rate | 9600 | 9600/~/115200 | PLC설정과 일치시킴. |
| Parity bit | Odd | Even, Odd, None | PLC설정과 일치시킴. |
| Data Bits | 8 | 7,8 | PLC설정과 일치시킴. |
| Stop Bits | 1 | 1, 2 | PLC설정과 일치시킴. |
| HMI Station No. | 4 | 4-7 | PLC설정과 일치시킴. |
| PLC Station No. | 1 | 0-3 | PLC설정과 일치시킴. |

PLC Setting:

| Communication mode | UniTelWay protocol, set PLC as master |
| --- | --- |

Wiring diagram:

1) TSX37-XX/TSX07-XX CPU

MT500 PLC [485]	TSX series CPU port

9P D-SUB Female	8P mini-din Female

| 1 | RX- |  | 2 | D- 8Pin miniDin Female |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | 1 | D+ |
| 5 | GND |  | 7 | GND |

COMMUNICATION MODULE: TSX P ACC01(for TSX37 series PLC)

MT500 PLC [485]	TSX P ACC01 Adapter

9P D-SUB Female	8P mini-din Female

| 1 | RX- |  | 2 | D- 8Pin miniDin Female |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | 1 | D+ |
| 5 | GND |  | 7 | GND |

2) RS485: CPU port

MT500 PLC [RS-485]	FB CPU port

9P D-SUB Female	15P D-SUB Male

| 1 | RX- |  | 7 | D- |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | 5 | D+ |

3) RS232: FB-DTBR/DTBR-E

MT500 PLC [232]	FB-DTBR/DTBR-E

9P D-SUB Male	15P D-SUB Male

| 2 | TXD |  | 1 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 2 | TXD |
| 5 | GND |  | 6 | GND |
|  |  |  | 3 | RTS |
|  |  |  | 4 | CTS |

4) RS485: FB-DTBR/DTBR-E

MT500 PLC [232]	FB-DTBR/DTBR-E

9P D-SUB Male	9P D-SUB Male

| 2 | TXD |  | 3 | RXD |
| --- | --- | --- | --- | --- |
| 3 | ### RXD |  | 2 | TXD |
| 5 | ### GND |  | 5 | ### GND |

5) RS485: FB-DTBR/DTBR-E

MT500 PLC [RS-485]	FB-DTBR/DTBR-E

9P D-SUB Female	3P Terminal Block

| 1 | RX- |  |  | D- |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  |  | ##### D+ |

6) RS232: FBs Port0

MT500 PLC [232]	FB-DTBR/DTBR-E

9P D-SUB Male	4P Mini-Din Male

| 2 | TXD |  | 4 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 3 | TXD 4P Mini-Din Female |
| 5 | GND |  | 2 | GND |

34.  SIEMENS S7 - 200

Siemens S7/200 series PLC (CPU212/214/215/216/221/222/224/226/226XM)

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | S7/200 |  |  |
| Com port | RS485 | RS485 |  |
| Baud rate | 9600 | 9600, 19200 | PLC설정과 일치시킴. |
| Parity bit | Even | Even, Odd, None | PLC설정과 일치시킴. |
| Data Bits | 8 | 7,8 | PLC설정과 일치시킴. |
| Stop Bits | 1 | 1, 2 | PLC설정과 일치시킴. |
| HMI Station No. | 0 | 0-255 |  |
| PLC Station No. | 2 | 0-255 | PLC설정과 일치시킴. |

PLC Setting:

| Communication mode | Set station number as 2 |
| --- | --- |

Wiring diagram:

MT500 PLC [485]	SIEMENS S7/200

CPU Port

9P D-SUB Female	9P D-SUB Female

| 1 | RX- |  | 8 | D- |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | 3 | D+ |
| 5 | GND |  | 5 | GND |

35.  SIEMENS S7/300(HMI Adapter)

Siemens S7/300 series PLC

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | SIEMENS S7/300 HMI Adapter | SIEMENS S7/300 HMI Adapter |  |
| Com port | RS232 | RS232/RS485 |  |
| Baud rate | 9600,19200 | 9600, 19200 | PLC설정과 일치시킴. |
| Parity bit | Odd | Odd | 고정. |
| Data Bits | 8 | 8 | 8 고정. |
| Stop Bits | 1 | 1, 2 | PLC설정과 일치시킴. |
| HMI Station No. | 0 | 0~255 |  |
| PLC Station No. | 2 | 0~255 | PLC설정과 일치시킴. |

PLC Setting:

| Communication mode | VB10 을 word영역으로 설정하여 사용함. |
| --- | --- |

Wiring diagram:

MT500 PLC [232]	SIEMENS S7/300 HMI

Adapter RS232 Port

9P D-SUB Female	9P D-SUB Male

| 2 | TXD |  | 2 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 3 | TXD |
| 5 | GND |  | 5 | GND |
|  |  |  | 7 | RTS |
|  |  |  | 8 | CTS |

36.  SIEMENS S7/300(PC Adapter)

Siemens S7/300 series PLC

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | SIEMENS S7/300 PC Adapter | SIEMENS S7/300 PC Adapter |  |
| Com port | RS232 | RS232/RS485 |  |
| Baud rate | 9600,19200 | 9600/~/115200 | PLC설정과 일치시킴. |
| Parity bit | Odd | Even, Odd, None | PLC설정과 일치시킴. |
| Data Bits | 8 | 7,8 | PLC설정과 일치시킴. |
| Stop Bits | 1 | 1, 2 | PLC설정과 일치시킴. |
| HMI Station No. | 0 | 0~255 |  |
| PLC Station No. | 2 | 0~255 | PLC설정과 일치시킴. |

PLC Setting:

| Communication mode |  |
| --- | --- |

Wiring diagram:

MT500 PLC [232]	SIEMENS S7/300 PC

Adapter RS232 Port

9P D-SUB Female	9P D-SUB Male

| 2 | TXD |  | 2 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 3 | TXD |
| 5 | GND |  | 5 | GND |
|  |  |  | 7 | RTS |
|  |  |  | 8 | CTS |

37.  SIMATIC TI505

SIMATIC TI505 Series PLCs: TI520, TI525, TI530, TI535, TI545, TI555, TI560, TI565, TI575

Using the NITP protocol in a point-to-point single master, single slave format.

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | SIMATIC TI505 |  |  |
| Com port | RS232 | RS232, RS485 (4W) |  |
| Baud rate | 19200 | 19200 |  |
| Parity bit | Odd | Odd |  |
| Data Bits | 7 | 7 |  |
| Stop Bits | 1 | 1 |  |
| HMI Station No. | 0 | 0 |  |
| PLC Station No. | 0 | 0 |  |

PLC Setting:

| Communication mode | NITP protocol |
| --- | --- |

Wiring diagram:

1) RS-232:

MT500 PLC [232]	SIMATIC TI505

9P D-SUB Male	25Pin D-SUB

| 2 | TXD |  | 3 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 2 | TXD |
| 5 | GND |  | 5 | GND |
|  |  |  | 4 | RTS |
|  |  |  | 5 | CTS |
|  |  |  | 6 | DSR |
|  |  |  | 8 | DCD |
|  |  |  | 20 | DTR |

2) RS-232:

MT500 PLC [232]	SIMATIC TI505

9P D-SUB Male	9Pin D-SUB

| 2 | TXD |  | 3 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 2 | TXD |
| 5 | GND |  | 5 | GND |
|  |  |  | 7 | RTS |
|  |  |  | 8 | CTS |
|  |  |  | 1 | DCD |
|  |  |  | 4 | DTR |
|  |  |  | 6 | DSR |

3) RS485 4W:

MT500 PLC [RS-485]	SIMATIC TI505

9P D-SUB Female	9Pin D-SUB

| 1 | RX- |  | 7 | DO (-) |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | 1 | DO (+) |
| 3 | TX- |  | 8 | DI (-) |
| 4 | TX+ |  | 5 | DI (+) |
| 5 | GND |  | 6 | GND |

38.  LG MASTER-K10S1

LG MASTER-K10S1

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | LG MASTER-K10S1 |  |  |
| Com port | RS232 | RS232/RS485 |  |
| Baud rate | 9600 | 9600 |  |
| Parity bit | None | None |  |
| Data Bits | 8 | 8 |  |
| Stop Bits | 1 | 1 |  |
| HMI Station No. | 0 | 0 |  |
| PLC Station No. | 0 | 0 |  |

PLC Setting:

| Communication mode | 9600, None, 8, 1 |
| --- | --- |

Wiring diagram:

MT500 PLC [232]	CPU port RS232

9P D-SUB Female	6P DIN Female

| 2 | TXD |  | 2 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 3 | TXD 6Pin miniDin male |
| 5 | GND |  | 5 | GND |

39.  LG MASTER-K60S

LG K10/30/60S

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | LG K60S |  |  |
| Com port | RS232 | RS232/RS485 | PLC설정과 일치시킴. |
| Baud rate | 9600 | 9600/~/115200 | PLC설정과 일치시킴. |
| Parity bit | None | Even, Odd, None | PLC설정과 일치시킴. |
| Data Bits | 8 | 7,8 | PLC설정과 일치시킴. |
| Stop Bits | 1 | 1,2 | PLC설정과 일치시킴. |
| HMI Station No. | 0 | 0~255 |  |
| PLC Station No. | 0 | 0~31 | PLC설정과 일치시킴 |

PLC Setting:

| Communication mode | 9600, None, 8, 1 |
| --- | --- |

Wiring diagram:

MT500 PLC [232]	CPU port RS232

9P D-SUB Male	9P D-SUB Male

| 2 | TXD |  | 2 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 3 | TXD |
| 5 | GND |  | 5 | GND |

40.  LG MASTER-K300S CPU 직결통신

LG MASTER-K series: K300S, K500S, K1000S

HMI Setting:

| Parameters | Recommend | Notes |
| --- | --- | --- |
| PLC type | LG MASTER-K300S |  |
| Com port | RS232 |  |
| Baud rate | 38400 |  |
| Parity bit | None |  |
| Data Bits | 8 |  |
| Stop Bits | 1 |  |
| HMI Station No. | 0 |  |
| PLC Station No. | 0 |  |

PLC Setting:

| Communication mode | 38400, None, 8, 1 |
| --- | --- |

Wiring diagram:

MT500 PLC [232]	CPU port RS232

9P D-SUB Male	9P D-SUB Male

| 2 | TXD |  | 2 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 3 | TXD |
| 5 | GND |  | 5 | GND |

41.  LG MASTER-K Cnet

LG MASTER-K series: K80S, K200S, K300S, K1000S: Communication Module (G7L-CUEB/G6L-CUEB/ G7L-CUEC/G6L-CUEC/G4L-CUEA/G3L-CUEA)

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | LG MASTER-KCNET |  |  |
| Com port | RS232 | RS232/RS485 | PLC설정과 일치시킴. |
| Baud rate | 19200 | 9600, 19200, 38400 | PLC설정과 일치시킴. |
| Parity bit | None | Even, Odd, None | PLC설정과 일치시킴. |
| Data Bits | 8 | 8 | PLC설정과 일치시킴. |
| Stop Bits | 1 | 1 | PLC설정과 일치시킴. |
| HMI Station No. | 0 |  |  |
| PLC Station No. | 0 | 0~31 | PLC설정과 일치시킴 |

PLC Setting:

| Communication mode | 19200, None, 8, 1 |
| --- | --- |

Wiring diagram:

1) RS232: Masterk 80S, 120S, 200S(K3P-07AS, K3P-07CS) series CPU Cnet Port

MT500 PLC [232]	CPU port Cnet I/F RS232

9P D-SUB Male	9P D-SUB Male

| 2 | TXD |  | 4 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 7 | TXD |
| 5 | GND |  | 5 | GND |

2) RS232: Communication module (G7L-CUEB/G6L-CUEB/G4L-CUEA/G3L-CUEA
CNET RS232)

MT500 PLC [232]	MASTER-K Cnet module

RS232 Port

9P D-SUB Male	9P D-SUB Male

| 2 | TXD |  | 2 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 3 | TXD |
| 5 | ### GND |  | 5 | GND |
|  |  |  | 1 | CD |
|  |  |  | 7 | RTS |
|  |  |  | 8 | CTS |
|  |  |  | 4 | DTR |
|  |  |  | 6 | DSR |

3) RS422: Communication module(G7L-CUEC/G6L-CUEC/G4L-CUEA/G3L-CUEA
CNET RS422/K3P-07BS)

MT500 PLC [RS-485]	MASTER-K Cnet module

RS422 Port

9P D-SUB Female	5P terminal

| 1 | RX- |  | ### SDB |
| --- | --- | --- | --- |
| 2 | RX+ |  | SDA |
| 3 | TX- |  | RDB |
| 4 | TX+ |  | RDA |
| 5 | GND |  | GND |

42.  LG GLOFA GM6 CPU 직결통신

LG GLOFA PLC: GM6 CPU

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | [PDS] LG GLOFA GM6 V3.00 |  |  |
| Com port | RS232 |  |  |
| Baud rate | 38400 |  |  |
| Parity bit | None |  |  |
| Data Bits | 8 |  |  |
| Stop Bits | 1 |  |  |
| HMI Station No. | 0 |  |  |
| PLC Station No. | 0 |  |  |

PLC Setting:

| Communication mode | 38400, None, 8, 1 |
| --- | --- |
| Device Register: | IX: nmb(dd): N(0-1) m(0-7) b(0-3) dd(0-15) QX: nmb(dd): N(0-1) m(0-7) b(0-3) dd(0-15) IW: nmb: N(0-1) m(0-7) b(0-3) QW: nmb: N(0-1) m(0-7) b(0-3) |

Wiring diagram:

MT500 PLC [232]	CPU port RS232

9P D-SUB Male	9P D-SUB Male

| 2 | TXD |  | 2 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 3 | TXD |
| 5 | GND |  | 5 | GND |

43.  LG GLOFA GM CNET & LG GOLFA Cnet Ver2.00

LG GLOFA-GM series: CPU(GM6/GM7)

Communication Module (G7L-CUEB/G6L-CUEB/G4L-CUEA/G3L-CUEA)

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | LG GLOFA Cnet | LG GLOFA Cnet Ver2.00 |  |
| Com port | RS232 | RS232/RS485 | PLC설정과 일치시킴. |
| Baud rate | 19200 | 9600/~/1152000 | PLC설정과 일치시킴. |
| Parity bit | None | Even, Odd, None | PLC설정과 일치시킴. |
| Data Bits | 8 | 8 | PLC설정과 일치시킴. |
| Stop Bits | 1 | 1 | PLC설정과 일치시킴. |
| HMI Station No. | 0 | 0~255 |  |
| PLC Station No. | 0 | 0~31 | PLC설정과 일치시킴 |

PLC Setting:

| Communication mode | 19200, None, 8, 1 |
| --- | --- |
| Device address(v2.00 ) | IX 0.1.12 = IX 01012, IX 0.1.31 = IX 01115 |

Wiring diagram:

1) RS-232: CPU port (GM6, GM7 series CPU Cnet port)

MT500 PLC [232]	LG GLOFA PLC

CPU Cnet RS232 Port

9P D-SUB Male	9P D-SUB Male

| 2 | TXD |  | 4 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 7 | TXD |
| 5 | GND |  | 5 | GND |

2) RS232: Communication module(G7L-CUEB/G6L-CUEB/G4L-CUEA/G3L-CUEA
CNET RS232)

MT500 PLC [232]	LG GLOFA PLC

Cnet module RS232 Po rt

9P D-SUB Male	9P D-SUB Male

| 2 | TXD |  | 2 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 3 | TXD |
| 5 | GND |  | 5 | GND |
|  |  |  | 1 | CD |
|  |  |  | 7 | RTS |
|  |  |  | 8 | CTS |
|  |  |  | 4 | DTR |
|  |  |  | 6 | DSR |

3) RS422: Communication module (G7L-CUEC/G6L-CUEC/G4L-CUEA/G3L-CUEA
CNET RS422)

MT500 PLC [RS-485]	LG GLOFA PLC

Cnet module RS422 Port

9P D-SUB Female	5P terminal

| 1 | RX- |  |  | SDB |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  |  | SDA |
| 3 | TX- |  |  | RDB |
| 4 | TX+ |  |  | RDA |
| 5 | GND |  |  | GND |

44.  TOSHIBA T series

Toshiba T series

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | Toshiba T serial |  |  |
| Com port | RS232 | RS232/RS485 | PLC설정과 일치시킴. |
| Baud rate | 9600 | 9600/~/115200 | PLC설정과 일치시킴. |
| Parity bit | Odd | Even, Odd, None | PLC설정과 일치시킴. |
| Data Bits | 8 | 7,8 | PLC설정과 일치시킴. |
| Stop Bits | 1 | 1, 2 | PLC설정과 일치시킴. |
| HMI Station No. | 0 | 0-255 |  |
| PLC Station No. | 0 | 0-255 | PLC설정과 일치시킴. |

| Online Simulator | YES |
| --- | --- |
| Direct Online Simulator | YES |
| Extend address mode | YES |

PLC Setting:

| Communication mode | Must set PLC node ID |
| --- | --- |

Wiring diagram:

- RS-232:

MT500 PLC [232]	Toshiba T1 PRG port

9P D-SUB Male	8P mini-D

| 2 | TXD |  | 8 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 6 | TXD |
| 5 | GND |  | 3 | GND |
|  |  |  | 4 | RTS |
|  |  |  | 7 | CTS |

- RS-232:

MT500 PLC [232]	Toshiba T2 PRG port

9P D-SUB Male	9P D-SUB Male

| 2 | TXD |  | 2 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 3 | TXD |
| 5 | GND |  | 5 | GND |
|  |  |  | 7 | RTS |
|  |  |  | 8 | CTS |

- RS-485:

MT500 PLC [RS-485]	Toshiba T2 LINK port

9P D-SUB Female	15P D-SUB Female

| 1 | RX- |  | 11 | TXB |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | 3 | TXA |
| 3 | TX- |  | 10 | RXB |
| 4 | TX+ |  | 2 | RXA |
| 5 | GND |  | 7 | SG |
|  |  |  | 5 | RTSA |
|  |  |  | 4 | CTSA |
|  |  |  | 13 | RTSB |
|  |  |  | 12 | CTSB |

45.  Matsushita FP

NAIS(Matsushita) FP series include FPΣ,FP0, FP1, FP2, FP2SH, FP10SH and FP3 & SAMSUNG N70, N700(알파계열)

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | Matsushita FP |  |  |
| Com port | RS232 | RS232/RS485 | PLC설정과 일치시킴. |
| Baud rate | 9600 | 9600/~/115200 | PLC설정과 일치시킴. |
| Parity bit | Odd | Even, Odd, None | PLC설정과 일치시킴. |
| Data Bits | 8 | 7 or 8 | PLC설정과 일치시킴. |
| Stop Bits | 1 | 1 or 2 | PLC설정과 일치시킴. |
| HMI Station No. | 0 | 0~255 |  |
| PLC Station No. | 1 | 0~255 | PLC설정과 일치시킴. FP3 must set 0. |

PLC Setting:

| Communication mode | 9600,O,8,1(default) |
| --- | --- |

Wiring diagram:

1) RS232:

MT500 PLC [232]	FPΣ, FP0, FP2, FP2SH,

FPM CPU Tool port

9P D-SUB Male	5P mini DIN RS-232

| 2 | TXD |  | 3 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 2 | TXD Mini Din 5 Pin Female |
| 5 | GND |  | 1 | GND |

2) RS232:

MT500 PLC [232]	FP0 CPU RS232

9P D-SUB Male	3P terminal

| 2 | TXD |  | ### R |
| --- | --- | --- | --- |
| 3 | RXD |  | S |
| 5 | GND |  | G |

3) RS232:

MT500 PLC [232]	FP1, FP2, FP2SH, FP10SH CPU

9P D-SUB Male	9P D-SUB Male RS232

| 2 | TXD |  | 3 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 2 | TXD |
| 5 | GND |  | 7 | GND |
|  |  |  | 4 | RTS |
|  |  |  | 5 | CTS |
|  |  |  | 8 | CD |
|  |  |  | 9 | ER |

4) RS485:

MT500 PLC [RS-485]	FP1 CPU RS422 port

9P D-SUB Female	Hirose 8Pin Port

| 1 | ### RX- |  | 2 | ### TXDB |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | 5 | TXDA |
| 3 | TX- |  | 3 | RXDB Hirose 8Pin Port |
| 4 | TX+ |  | 6 | RXDA |
| 5 | GND |  | 1 | GND |

5) RS485:

MT500 PLC [RS-485]	FP3 CPU RS422 port

9P D-SUB Female	15P D-SUB Female

| 1 | ### RX- |  | 9 | TXDB |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | 2 | TXDA |
| 3 | TX- |  | 10 | RXDB |
| 4 | TX+ |  | 3 | RXDA |
| 5 | GND |  | 7 | GND |
|  |  |  | 4 | RTS+ |
|  |  |  | 5 | CTS+ |
|  |  |  | 11 | RTS- |
|  |  |  | 12 | CTS- |

46.  DELTA DVP PLC

DELTA DVP series

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | DELTA DVP |  |  |
| Com port | RS232 | RS232, RS485 |  |
| Baud rate | 9600 | 9600, 19200 |  |
| Parity bit | Even | Even, Odd, None |  |
| Data Bits | 7 | 7, 8 |  |
| Stop Bits | 1 | 1 |  |
| HMI Station No. | 0 |  |  |
| PLC Station No. | 1 | 0~255 |  |

PLC Setting:

| Communication mode | 9600,O, 8,1(default) |
| --- | --- |

Wiring diagram:

MT500 PLC [232]	DELTA DVP CPU port

9P D-SUB Male	8p mini DIN

| 2 | TXD |  | 5 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 4 | TXD |
| 5 | GND |  | 3 | GND 8p mini DIN |

47. SAMSUNG N70+, N700+

N70+, N700+ series

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | Samsung SPC-10 |  |  |
| Com port | RS-232 | RS232/RS485 | PLC설정과 일치시킴. |
| Baud rate | 9600 | 9600/~/115200 | PLC설정과 일치시킴. |
| Parity bit | None | Even, Odd, None | PLC설정과 일치시킴. |
| Data Bits | 8 | 7 or 8 | PLC설정과 일치시킴. |
| Stop Bits | 1 | 1 or 2 | PLC설정과 일치시킴. |
| HMI Station No. | 192 | 0~255 |  |
| PLC Station No. | 1 | 0~255 | Default=1 |

PLC Setting:

| Communication mode | 9600,N, 8,1(default) |
| --- | --- |

Wiring diagram:

1) RS232:

MT500 PLC [232]	SAMSUNG CPU port

9P D-SUB Male	9 Pin D Male

| 2 | TXD |  | 3 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 2 | TXD |
| 5 | GND |  | 5 | GND |

48. SAMSUNG SPC-10

Samsung SPC-10

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | Samsung SPC-10 |  |  |
| Com port | RS485 |  |  |
| Baud rate | 9600 |  |  |
| Parity bit | None |  |  |
| Data Bits | 8 |  |  |
| Stop Bits | 1 |  |  |
| HMI Station No. | 192 |  |  |
| PLC Station No. | 255 |  |  |

PLC Setting:

| Communication mode |  |
| --- | --- |

Wiring diagram:

MT500 PLC [RS-485]	Samsung SPC-10

CPU port

9P D-SUB Female	8Pin mini DIN

| 1 | RX- |  | 6 | TR- |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | 7 | TR+ 8p mini DIN |
| 5 | GND |  | 5 | GND |

49.  HITACHI H series (CPU port)

HITACHI H series: EH-150, Micro-EH, H20, H40, H64, H200, H250, H252, H300, H302, H700, H702, H1000, H1002, H2000, H4010

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | HITACHI |  |  |
| Com port | RS232 | RS232, RS485 | PLC 설정과 일치시킴. |
| Baud rate | 19200 | 9600, 19200, 38400 | PLC 설정과 일치시킴. |
| Parity bit | Even | Even | PLC 설정과 일치시킴. |
| Data Bits | 7 | 7 | PLC 설정과 일치시킴. |
| Stop Bits | 1 | 1 | PLC 설정과 일치시킴. |
| HMI Station No. | 0 | 0-255 | 설정 없음. |
| PLC Station No. | 0 | 0-255 | 설정 없음. |

| Online Simulator | OK |
| --- | --- |
| Direct Online Simulator | OK |
| Extend address mode | Does not Support |

PLC Setting:

| Communication mode Select | 19200,E, 7, 1(default) |
| --- | --- |

Wiring diagram:

WARNING: If your communications cable is not wired exactly as shown in our cable assembly instructions, damage to the MT500 or loss of communications can result.

| CPU TYPE | Port 1 | Port 2 |
| --- | --- | --- |
| EH-150/CPU 104A | RS-232 | RS-232 |
| EH-150/CPU 208A | RS-232 | RS-232 |
| EH-150/CPU 308A | RS-232/RS-485 | RS-232 |
| EH-150/CPU 316A | RS-232/RS-485 | RS-232 |
| EH-150/CPU 448A | RS-232/RS-485 | RS-232 |

| Port setting toggle - switch Mode setting DIP-switch Switch Number |  |  |  |  |
| --- | --- | --- | --- | --- |
| 1 | OFF | Normal mode |  |  |
| 2 | OFF | TRNS0 operation |  |  |
| 3, 4 | 3 | 4 | Port1 transmission speed |  |
|  | ON | ON | 4,800 bps | 지원안함 |
|  | OFF | ON | 9,600 bps |  |
|  | ON | OFF | 19,200 bps | 기본값 |
|  | OFF | OFF | 38,400 bps |  |
| 5 | ON | Dedicated port |  |  |
| 6 | 6 | PHL | Port2 transmission speed |  |
|  | ON | Low | 9,600 bps |  |
|  | ON | High | 38,400 bps |  |
|  | OFF | Low | 4,800 bps | 지원안함 |
|  | OFF | High | 19,200 bps | 기본값 |
| 7 | OFF | (System mode) |  | 변경안함 |
| 8 | OFF | (System mode) |  | 변경안함 |

EH-150 port1 RS232

MT500 PLC [232]	HITACHI EH-150 port1

9P D-SUB Male	8pin RJ45 Male

| 2 | TXD |  | 6 | #### RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 5 | TXD |
| 5 | GND |  | 1 | SG |
| 7 | CTS |  | 8 | RS |
| 8 | RTS |  | 7 | DR |

EH-150 port1 RS485 4wire (RS422)

MT500 PLC [485]	HITACHI EH-150 port1

9P D-SUB Female	8pin RJ45 Male

| 1 | RX- |  | 5 | TX- |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | 4 | TX+ |
| 3 | TX- |  | 6 | RX- |
| 4 | TX+ |  | 7 | RX+ |
| 5 | GND |  | 1 | GND |

MT500 PLC [232]

9P D-SUB Male

| 7 | ### CTS |
| --- | --- |
| 8 | RTS |

EH-150 RS-485 connect must short the PLC [232] port pin 7,8.

EH-150 port1 RS485 2wire

MT500 PLC [485]	HITACHI EH-150 port1

9P D-SUB Female	8pin RJ45 Male

| 1 | RX- |  | 5 | TX- |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | 4 | TX+ |
| 3 | TX- |  | 6 | RX- |
| 4 | TX+ |  | 7 | RX+ |
| 5 | GND |  | 1 | GND |

MT500 PLC [232]

9P D-SUB Male

| 7 | ### CTS |
| --- | --- |
| 8 | RTS |

EH-150 RS-485 connect must short the PLC [232] port pin 7,8.

EH-150 port2 RS232

MT500 PLC [232]	HITACHI EH-150 port2

9P D-SUB Male	8pin RJ45 Male

| 2 | TXD |  | 6 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 5 | TXD |
| 5 | GND |  | 1 | GND |
| 7 | CTS |  | 8 | RS |
| 8 | RTS |  | 7 | DR |

H series CPU RS232 port

MT500 PLC [232]	HITACHI H series CPU RS232

9P D-SUB Male	15p D-SUB Male

| 2 | TXD |  | 3 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 2 | TXD |
| 5 | GND |  | 9 | GND |
| 7 | CTS |  | 4 | RTS |
|  |  |  | 10 | SG |
|  |  |  | 5 | CTS |
|  |  |  | 7 | DSR |
|  |  |  | 8 | PHL |
|  |  |  | 14 | PV12 |

MT500 PLC [485]	CPU port RS422

9P D-SUB Female	8P RJ45

| 1 | RX- |  | 4 | TX- |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | 3 | TX+ |
| 3 | TX- |  | 6 | RX- 8-Pin RJ45 Cannecter (8P9C) |
| 4 | TX+ |  | 5 | RX+ |
| 5 | GND |  |  |  |

50.  FUJI NB Series

KV series PLC: KV-10, KV-16, KV-24, KV-40

HMI Setting:

| PLC type | [pds] Fuji NB Series |
| --- | --- |
| Com port setting | RS485, 19200, Odd, 8,1 |
| HMI Node number | 0 (none) |
| PLC Node number | 0 (none) |
| Parameter 1 | PLC Password (default is 0) |

PLC Setting:

| Communication mode Select | 19200,E,8,1 |
| --- | --- |

Wiring diagram:

MT500 PLC [485]	CPU port RS422

9P D-SUB Female	8P RJ45

| 1 | RX- |  | 4 | TX- |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | 3 | TX+ |
| 3 | TX- |  | 6 | RX- 8-Pin RJ45 Connecter (8P9C) |
| 4 | TX+ |  | 5 | RX+ |
| 5 | GND |  |  |  |

51.  Keyence

KV series PLC: KV-10, KV-16, KV-24, KV-40

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | Keyence KV-16DT |  |  |
| Com port | RS232 |  |  |
| Baud rate | 9600 | 9600 |  |
| Parity bit | Even | Even, Odd, None |  |
| Data Bits | 8 | 8 |  |
| Stop Bits | 1 | 1 |  |
| HMI Station No. | 0 |  |  |
| PLC Station No. | 0 | None |  |

PLC Setting:

| Communication mode |  |
| --- | --- |

Wiring diagram:

1) RS-232:

MT500 PLC [232]	KV CPU port

9P D-SUB Male	RJ11

| 2 | TXD |  | 5 | RXD Pin assignment for the KV |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 3 | TXD |
| 5 | GND |  | 4 | GND |

52.  SHARP JW [pds]

SHARP JW Series PLC

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | [pds]Sharp JW Series |  |  |
| Com port | RS485 | RS485 |  |
| Baud rate | 19200 | 19200 |  |
| Parity bit | None | Even, Odd, None |  |
| Data Bits | 7 | 7 |  |
| Stop Bits | 1 | 1 |  |
| HMI Station No. | 0 | 0 |  |
| PLC Station No. | 1 | 1-63 | PLC default is 1 |

Wiring diagram:

RS-485:

MT500 PLC [RS-485]	SHARP JW

9P D-SUB Female	Communication Port

| 1 | RX- |  | L2 |
| --- | --- | --- | --- |
| 2 | RX+ |  | L1 |
| 5 | GND |  |  |

53.  YOKOGAWA PLC Series

KV series PLC: KV-10, KV-16, KV-24, KV-40

HMI Setting:

| PLC type | YOKOGAWA PLC Series V1.0 |
| --- | --- |
| Com port setting | RS232, 19200, E, 8, 1 (PLC 설정과 일치) |
| Parameter2 | 10 |
| PLC Station No | 1 |

PLC Setting:

| Communication mode | 19200,E,8,1 (PLC 설정과 일치) |
| --- | --- |
| Select | Use Personal Communication Link |
| Select | Use checksum |
| Select | Use End Character |

MT500 PLC [232]	CPU module

9P D-SUB Male	RS-232

| 2 | TX |  | 2 | RD |
| --- | --- | --- | --- | --- |
| 3 | RX |  | 3 | TD |
| 5 | GND |  | 5 | GND |

MT500 PLC [232]	통신카드

9P D-SUB Male	RS-232

| 2 | TX |  | 2 | RD |
| --- | --- | --- | --- | --- |
| 3 | RX |  | 3 | SD |
| 5 | GND |  | 5 | SG |
|  |  |  | 4 | ER |
|  |  |  | 6 | DR |
|  |  |  | 7 | RS |
|  |  |  | 8 | CS |

MT500 PLC [RS-485]	통신카드

9P D-SUB Female	RS-422 5P terminal

| 1 | RX- |  | ### SDB |
| --- | --- | --- | --- |
| 2 | RX+ |  | SDA |
| 3 | TX- |  | RDB |
| 4 | TX+ |  | RDA |
| 5 | GND |  | GND |

54.  Memory Map protocol

MT500 series

Easy-View의 Memory to Memory  통신은 IBM3764R통신방식을 기준으로 합니다.

Easy-View의 DATA는 512Word이며,

Memory to Memory Protocol 사용 시 HOST와 접속된Easy-View는 Data Memory에 Data를 보내고 Easy-View는 그 Data를 작화 된 형식으로 표현 합니다.

또한, 사용자는 Easy-View에서 제공되는 Tag형식으로 Data를 설정 및 변경할 수 있습니다.

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | Memory Map Master Memory Map Slave |  |  |
| Com port | RS232 | RS232, RS485 4W, 2W | RS485 default = RS485 4W |
| Baud rate | 19200 | 9600~115200 | RS485 2W Only 9600, 19200 |
| Parity bit | Even | Even, Odd, None |  |
| Data Bits | 8 |  |  |
| Stop Bits | 1 |  |  |
| HMI Station No. | 0 |  |  |
| PLC Station No. | 0 |  |  |

Select one of the following from the Driver list in the System Parameters settings:

Memory Map Master:

The MT-500 commands take precedence whenever there is a “collision” on

The communications lines. The Host must wait for all clear and then send commands.

Memory Map Slave:

The Host commands take precedence whenever there is a “collision” on the

Communications lines. The MT-500 must wait for all clear and then send commands.

Wiring diagram:

RS-232:

MT500 PLC [232]	MT500 PLC [232]

9P D-SUB Male	9P D-SUB Male

| 2 | TX |  | 3 | RX |
| --- | --- | --- | --- | --- |
| 3 | RX |  | 2 | TX |
| 5 | GND |  | 5 | GND |

RS-485 4W:

MT500 PLC [RS-485]	MT500 PLC [RS-485]

9P D-SUB Female	9P D-SUB Female

| 1 | RX- |  | 3 | TX- |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | 4 | TX+ |
| 3 | TX- |  | 1 | RX- |
| 4 | TX+ |  | 2 | RX+ |
| 5 | GND |  | 5 | GND |

RS-485 2W:

MT500 PLC [RS-485]	MT500 PLC [RS-485]

9P D-SUB Female	9P D-SUB Female

| 1 | RX- |  | 1 | RX- |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | 2 | RX+ |
| 5 | GND |  | 5 | GND |

Memory to Memory 통신상의 제어방식

Command Data는 모두 binary입니다.

모든 Command는 양방향이며, 그것은 HOST로부터 Easy-View로 보냅니다.

BCC의 전송DATA는 XOR로 취합니다.(DEL,ETX포함)

Read/Writ Command의 “addr”는word address(0-511)로 지정 됩니다.

전송 data 값이 10h일 때, DLE code와 같으므로 10h를 중복전송 해야 합니다.

| (통신 code) STX | DLE | ACK | NAK | ETX |
| --- | --- | --- | --- | --- |
| 02h | 10h | 06h | 15h | 03h |

55.  IIS ESC

INDUSTRIAL INDEXING SYSTEMS, INC. Emerald EMC-2000 controller

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | IIS ESC |  |  |
| Com port | RS232 | RS232, RS485 |  |
| Baud rate | 19200 | 9600~115200 |  |
| Parity bit | None |  |  |
| Data Bits | 8 |  |  |
| Stop Bits | 1 |  |  |
| HMI Station No. | 0 |  |  |
| PLC Station No. | 0 |  |  |

PLC Setting:

| Communication mode | App Port set Mode: ESC Packet Protocol 19200, None, 8, 1 |
| --- | --- |

Wiring diagram:

RS-232:

MT500 PLC [232]	EMC-2000 Port 2

9P D-SUB Male	RJ11

| 1 | TXD |  | 3 | RXD |
| --- | --- | --- | --- | --- |
| 2 | RXD |  | 5 | TXD |
| 5 | GND |  | 4 | GND |

56.  Jetter-Nano

Jetter Nano

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | Jetter-Nano |  |  |
| Com port | RS232 |  |  |
| Baud rate | 9600 |  |  |
| Parity bit | Even | Even, Odd, None |  |
| Data Bits | 8 | 8 |  |
| Stop Bits | 1 | 1 |  |
| HMI Station No. | 0 |  |  |
| PLC Station No. | 0 |  |  |

PLC Setting:

| Communication mode | 9600, Even, 8, 1 |
| --- | --- |

Wiring diagram:

RS-232:

MT500 PLC [232]	Jetter Nano PC port

9P D-SUB Male	9P D-SUB Female

| 2 | TXD |  | 3 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 2 | TXD |
| 5 | GND |  | 7 | GND |

57.  Lenze

PLC Model No.: 9300/8200 series

Pass-through 2102IB field bus module: RS485 (LECOM B)

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | Lenze |  |  |
| Com port | RS485 | RS485 |  |
| Baud rate | 9600 | 9600, 19200 |  |
| Parity bit | Even | Even, Odd, None |  |
| Data Bits | 7 | 7,8 |  |
| Stop Bits | 1 | 1, 2 |  |
| HMI Station No. | 0 | 0-255 |  |
| PLC Station No. | 1 | 0-255 |  |

PLC Setting:

| Communication mode | Same as the MT500 setting |
| --- | --- |

Wiring diagram:

MT500 PLC [485]	Lenze 2102IB

LECOM -B RS485

9P D-SUB Female	Plug-in terminal 4-pole

| 1 | RX- |  | 72 T/R (B) |
| --- | --- | --- | --- |
| 2 | RX+ |  | 71 T/R (A) |

58.  LIYAN EX Series

- LIYAN PLC Ex/Ex1s/Ex1n/Ex2n series

- HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | MITSUSBISHI FX0n/FX2 |  |  |
| Com port | RS232 | RS232 | PLC설정과 일치시킴. |
| Baud rate | 9600 | 9600/~/115200 | PLC설정과 일치시킴. |
| Parity bit | Even | Even, Odd, None | PLC설정과 일치시킴. |
| Data Bits | 7 | 7,8 | PLC설정과 일치시킴. |
| Stop Bits | 1 | 1,2 | PLC설정과 일치시킴. |
| HMI Station No. | 0 | 0~255 |  |
| PLC Station No. | 0 | 0~255 | PLC설정과 일치시킴. |

- PLC Setting:

| Communication mode | 9600, 7, 1,Even |
| --- | --- |

- Wiring diagram:

- Ex, Ex1s, Ex1n, Ex2n series RS232

MT500 PLC [232]	LIYAN Ex series PLC

CPU RS232 Port

9P D-SUB Male	8P miniDin Female

| 2 | TXD |  | 7 | RXD 8Pin miniDin Female |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 2 | ### TXD |
| 5 | GND |  | 3 | GND |

59.  VIGOR

VIGOR M Series

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | VIGOR |  |  |
| Com port | RS232 | RS232, RS485 4wires, |  |
| Baud rate | 19200 |  |  |
| Parity bit | Even |  |  |
| Data Bits | 7 |  |  |
| Stop Bits | 1 |  |  |
| HMI Station No. | 0 |  |  |
| PLC Station No. | 1 |  |  |

PLC Setting:

| Communication mode | None |
| --- | --- |

Wiring diagram:

RS-485 4wire:

MT500 PLC [485]	VIGOR M series

9P D-SUB Female	6pin terminal

| 1 | ### RX- |  | TX- |
| --- | --- | --- | --- |
| 2 | RX+ |  | TX+ |
| 3 | TX- |  | RX- |
| 4 | TX+ |  | RX+ |
| 5 | GND |  | SG |
|  |  |  | 24V |

RS-232:

MT500 PLC [232]	VIGOR M series

9P D-SUB Male	COM Port

| 2 | TX |  | 2 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RX |  | 3 | TXD |
| 5 | GND |  | 5 | GND |

- 60.  TAIAN TP02 Series

TAIAN PLC TP02 series

- HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | Taian TP02 |  |  |
| Com port | RS485 4W/2W | RS485 4W/2W | MMI 422 port: 4W; RS485 terminals:2W |
| Baud rate | 19200 | 9600,19200,38400 | PLC설정과 일치시킴 |
| Parity bit | Even | Even, Odd, None | PLC설정과 일치시킴 |
| Data Bits | 7 | 7,8 | PLC설정과 일치시킴 |
| Stop Bits | 2 | 1,2 | PLC설정과 일치시킴 |
| HMI Station No. | 0 | 0-255 |  |
| PLC Station No. | 1 | 0-255 | PLC설정과 일치시킴 |

- PLC Setting:

| Communication mode | 19200,7,2,Even |
| --- | --- |

RS422 port:WS041=120,WS042=1; 	RS485 terminals:WS044=120,WS045=1.

- Wiring diagram:

TP02 Series MMI RS422 Port:

MT500 PLC [485]	Tainan TP02 series PLC

CPU RS422 Port

9P D-SUB Female	9P D-SUB Male

| 1 | RX- |  | 8 | TX- |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | 3 | TX+ |
| 3 | TX- |  | 7 | RX- |
| 4 | TX+ |  | 2 | RX+ |

TP02 Series RS485 Terminals

MT500 PLC [485]	Tainan TP02 series PLC

9P D-SUB Female	RS485 Terminals

| 1 | RX- |  | T/R- |
| --- | --- | --- | --- |
| 2 | RX+ |  | T/R+ |

- 61.  SAIA PCD PGU modes

SAIA PCD series PGU mode.

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | SAIA PCD PGU mode | SAIA PCD S-BUS mode | PDS driver |
| Com port | RS232 | RS232, RS485 |  |
| Baud rate | 9600 | 9600, 19200 |  |
| Parity bit | Even | Even, Odd, None |  |
| Data Bits | 7 | 7, 8 |  |
| Stop Bits | 1 | 1 |  |
| HMI Station No. | 0 |  |  |
| PLC Station No. | 1 | 0-255 |  |

PLC Setting:

| Communication mode | 9600,E, 7, 1(default) |
| --- | --- |

Wiring diagram:

RS232:

MT500 PLC [232] 	SAIA PCD PGU port

9P D-SUB Male	9P D-SUB Male

| 2 | TXD |  | 2 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 3 | TXD |
| 5 | GND |  | 5 | GND |
| 8 | RTS |  | 6 | DSR |
|  |  |  | 7 | RTS |
|  |  |  | 8 | CTS |

62.  SAIA PCD S-Bus mode

SAIA PCD series S-Bus mode.

HMI Setting:

| Parameters | Recommend | Option | Notes |
| --- | --- | --- | --- |
| PLC type | SAIA PCD S-BUS mode | SAIA PCD PGU mode | PDS driver |
| Com port | RS232 | RS232, RS485 |  |
| Baud rate | 9600 | 9600, 19200, 38400 |  |
| Parity bit | None | Even, Odd, None |  |
| Data Bits | 8 | 7, 8 |  |
| Stop Bits | 1 | 1 |  |
| HMI Station No. | 0 |  |  |
| PLC Station No. | 1 | 0-255 |  |

PLC Setting:

| Communication mode | 9600,N, 8,1(default), |
| --- | --- |
| RS232 | Port 0-Type: RS23 |
| RS485 2W | S-BUS Mode: Data (S2), Port 0-Type: RS485 |

Wiring diagram:

RS232:

MT500 PLC [232] 	SAIA PCD PGU port

9P D-SUB Male	9P D-SUB Male

| 2 | TXD |  | 2 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 3 | TXD |
| 5 | GND |  | 5 | GND |
| 8 | RTS |  | 6 | DSR |
|  |  |  | 7 | RTS |
|  |  |  | 8 | CTS |

RS485:

MT500 PLC [RS-485]	SAIA PCD

9P D-SUB Female	Interface no.0

| 1 | RX- |  | 29 |
| --- | --- | --- | --- |
| 2 | RX+ |  | 28 |

63. Cimon CM2 Series

CIMON PLC series (LINK)/ CP4C(CPU RS232)/ CP4D(CPU RS485 4W)

HMI Setting:

| PLC type | [PDS]CIMON PLC series (LINK) |
| --- | --- |
| Com port setting | RS485 4W, 9600~38400, None, 8, 1 |
| HMI Node number | 0 (none) |
| PLC Node number | 0 (none) |

PLC Setting:

| Communication mode | 38400,N, 8,1(default), |
| --- | --- |

Wiring diagram:

RS232:

MT500 PLC [232] 		SAIA PCD PGU port

9P D-SUB Male	8P RJ45

| 2 | TXD |  | 5 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RXD |  | 6 | TXD |
| 5 | GND |  | 4 | GND |

RS485:

MT500 PLC [485]		PLC

| 9P D-SUB Female |  |  | 통신카드 RS485 4W | 8P RJ45 | CPU RS485 4W |
| --- | --- | --- | --- | --- | --- |
| 1 | RX- |  | 2 | SDB | 2 |
| 2 | RX+ |  | 1 | SDA | 1 |
| 3 | TX- |  | 4 | RDB | 5 8-Pin RJ45 Connecter (8P9C) |
| 4 | TX+ |  | 3 | RDA | 3 |
| 5 | GND |  | 5 | GND | 8 |

64. OMRON CJ1/CS1

OMRON CJ1M, CJ1H, CJ1G, CS1H and CS1G. (Host Link Protocol FINS command),

확장 어드레스 모드

HMI Setting:

| Parameters | Recommend | Option |
| --- | --- | --- |
| PLC type | [PDS]OMRON CJ1/CS1 V1.2 |  |
| Com port | RS232 | RS232, RS422, RS485 |
| Baud rate | 9600 | 9600, 19200 |
| Parity bit | Even | Even, Odd, None |
| Data Bits | 7 | 7 or 8 |
| Stop Bits | 2 | 1 or 2 |
| HMI Station No. | 0 |  |
| PLC Station No. | 0 | 0-31 |

| PLC Setting: Communication mode | HOSTLINK protocol |
| --- | --- |

Wiring diagram:

RS-232: MT500 PLC [232]	OMRON CPU

9P D-SUB Male	RS-232 9P D-SUB Male

| 2 | TX |  | 3 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RX |  | 2 | TXD |
| 5 | GND |  | 9 | GND |
|  |  |  | 4 | RTS |
|  |  |  | 5 | CTS |

RS-485: CJ1M, CJ1H, CJ1G, CS1H and CS1G

MT500 PLC [RS-485]	OMRON

9P D-SUB Male	Station 1

| 1 | RX- |  | 1 | SDB |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | 2 | SDA |
|  |  |  | Station 2 |  |
|  |  |  | 1 | SDB |
|  |  |  | 2 | SDA |

65.  MITSUBISHI FX3U

Mitsubishi FX3U(C) series PLC

HMI Setting:

| PLC type | MITSUBISHI FX3U [PDS V1.10] |
| --- | --- |
| Com port setting | RS485 4W, 9600, E, 7, 1 |
| HMI Node number | 0 (none) |
| PLC Node number | 0 (none) |

PLC Setting:

| Communication mode Select | 9600, E, 7, 1(default) |
| --- | --- |

Wiring diagram:

MT500 PLC [RS-485]	Mitsubishi FX 3U CPU

RS422 Port

9P D-SUB Female	8P MiniDin Male

| 1 | RX- |  | 4 | TX- |
| --- | --- | --- | --- | --- |
| 2 | RX+ |  | 7 | TX+ |
| 3 | TX- |  | 1 | RX- 8Pin miniDin Female |
| 4 | TX+ |  | 2 | RX+ |
| 5 | GND |  | 3 | GND |

66.  MITSUBISHI FX3U 485BD/485ADP

Mitsubishi FX3U 485BD/ 485ADP

HMI Setting:

| PLC type | Mitsubishi FX0n/2/2n COM |  |  |
| --- | --- | --- | --- |
| Com port setting | RS485 4W, 19200, E, 7, 1 |  |  |
| HMI Station number | 0 | PLC Station number | 1 (none) |

PLC Setting: Operate communication setting: 체크

| CH1설정 | RS-485, 19200 , Even, 7, 1, Sum check |  |  |
| --- | --- | --- | --- |
| Protocol | Dedicated | Transmission control procedure | Form1 |
| Station | 01H | Time out judge time | 1 |

Wiring diagram:

Communi station Module RS485BD:

MT500 PLC [RS-485] 	RS485BD Module

9P D-SUB Female	5P terminal

| 1 | RX- |  | SDB |
| --- | --- | --- | --- |
| 2 | RX+ |  | SDA |
| 3 | TX- |  | RDB |
| 4 | TX+ |  | RDA |
| 5 | GND |  | SG |

67.  MITSUBISHI Q02H/Q06H CPU

Mitsubishi Q00 and Q01 CPU.

HMI Setting:

| PLC type | MITSUBISHI Q CPU Direct[PDS V2.00] |
| --- | --- |
| Com port setting | RS232, 9600~115200, Odd, 8, 1 |
| HMI Node number | 0 (none) |
| PLC Node number | 0 (none) |

PLC Setting:

| Communication mode Select | RS232, 9600~115200, Odd, 8, 1(기본 설정 값) |
| --- | --- |

Wiring diagram:

RS-232:

MT500 PLC [232]	Q02H/Q06H CPU

RS232 port

9P D-SUB Male	Mini-DIN 6Pin Male

| 2 | TX |  | 1 | RXD |
| --- | --- | --- | --- | --- |
| 3 | RX |  | 2 | MINI-DIN 6PIN Female PLC측 PIN번호 TXD |
| 5 | GND |  | 3 | GND |

* 통신드라이버 (MITSUBISHI Q CPU Direct[PDS V2.00]받는 곳:

http://www.enterst.co.kr 사이트 접속 후 자료실/소프트웨어/[이지뷰]-HMI<-->MITSUBISHI Q02,06H CPU직결통신 프로토콜 선택함.

* 다운받은 압축파일을 C:\EB500\V272U\Drivers\에 풀어줌.

68.  SIEMENS S7/300(MPI Adapter)

Siemens S7/300 series PLC

HMI Setting:

| PLC type | SIEMENS S7/300 PC Adapter |  |  |
| --- | --- | --- | --- |
| Com port setting | RS232, 19200, Odd, 8, 1 |  |  |
| HMI Node number | 0 | PLC Node number | 2 |

PLC Setting:

| Communication mode | MPI Transmission rate(187.5 kbps) |
| --- | --- |

Wiring diagram: MT5-MPI Cable 사용하여 통신함.

제 7장 MT의 Local Data 영역

Local Bit(LB), Local Word(LW), Recipe Word(RW) 등은 다음과 같은 기능 이외로는 사용할 수 없습니다.

Local Bits : 9000~9999, Local Words : 9000~9999, Recipe Words : 60000~65535

1 Local Bit (LB)

LB0000 ~ LB8999 ( User용)	LB9000 ~ (시스템 내부용)

| 위 치 | 설 명 | 비 고 |
| --- | --- | --- |
| 9000 ~ 9009 | 상시 ON | Numeric Input의 Trigger Bit로 활용 (읽기/쓰기) |
| 9010 | Recipe Memory에 download 표시 | Recipe Memory에 download중 ON, Download 완료 후 OFF (읽기) |
| 9011 | Recipe Memory에 Upload 표시 | Recipe Memory에 Upload 중 ON, Upload 완료 후 OFF (읽기) |
| 9012 | Recipe Memory에 Upload, Download할 때 표시 | Recipe Memory에 전송 MT로 download전송 때 ON, 설정 완성될 때 OFF (읽기) |
| 9013 | Touch indicator | 화면에Touch할 때 ON됨 -> (읽기) |
| 9014 | CPU indicator | CPU 사용 시ON (읽기) |
| 9015 | Alarm indicator | 화면에 Alarm발생시 ON (읽기) -> |
| 9016 | Printer Error Indicate | 프린터 이상시 ON, 정상일때 OFF (읽기) |
| 9017 | Printer Control | ON일 때, 프린터 사용 불가, OFF일 때 프린터 사용 가능 System Parameter에서 Printer 설정 후 사용가능 (읽기/쓰기) |
| 9020 | Pen | Message Board사용 시 Pan 설정 ON (읽기/쓰기) |
| 9021 | Brush | Message Board사용 시 Brush 설정 ON (읽기/쓰기) |
| 9022 | Clipping | Message Board 사용 시 Clipping 설정 ON (읽기/쓰기) |
| 9030 | Pen width Pixel 1 | Message Board 사용 시 Pen의 굵기 선택 (1 Pixel ; 1화소) (읽기/쓰기) |
| 위 치 | 설 명 | 비 고 |
| 9031 | Pen width Pixel 2 | Message Board사용 시 Pen의 굵기 선택 (2 Pixel; 2화소) (읽기/쓰기) |
| 9032 | Pen width Pixel 3 | Message Board 사용 시 Pen의 굵기 선택 (3 Pixel ; 3화소) (읽기/쓰기) |
| 9040 | Fast select screen Icon (숨김/표시) | ON일 때 화면(Window)을 숨김 OFF 일 때, 화면(Window)이 표시됨. (읽기/쓰기) |
| 9041 | Task Bar (숨김/표시) | ON일 때, Task Bar를 숨김, OFF 일 때, Task Bar가 표시됨 (읽기/쓰기) |
| 9042 | Task Button (숨김/표시) | ON일 때, Task Button을 숨김 OFF 일 때, Task Button이 표시됨 (읽기/쓰기) |
| 9043 | Fast select Screen Task Bar Task Button (숨김/표시) | ON일 때Fast select Screen/Task Bar/Task Button 을 동시에 숨김. OFF일 때Fast select Screen/ Task Bar/Task Button이 동시에 표시됨. (읽기/쓰기) |
| 9044 | System Parameters를 Recipe 메모리에 저장기능 | ON일 때, System Parameters 를 Recipe 메모리에 저장됨.이후 system 셋팅된후 현재 BIT가 OFF됨. (읽기/쓰기) |
| 9045 | MT 재시작. | ON일 때, MT 재시작. 재시작 후 BIT가 OFF됨. (쓰기) |
| 9046 | Low security level |  |
| 9050 | 도시바 T/C 쓰기 허용비트 | ON일 때, 타이머/카운터 사용가능 |
| 9051 | Back Light가 OFF일 때, Touch 기능 사용여부 설정 | ON일 때 Back Light OFF중 화면의 Touch기능이 동작 안됨, OFF시 Back Light OFF중 화면의 Touch기능이 동작됨 (읽기/쓰기) |
| 9052 | MT의 현재 화면번호를 PLC로 재전송 허용 여부 | PLC Control에서 화면(Window)을 전환할 때, 현재의 화면번호를 PLC로 전송 여부. ON일 때 사용 안 함 (Change Window편 참조) |
| 9055 | MT와 PLC통신 상태 | ON (통신 중)/OFF (통신 안됨)로 나타냄. (읽기/쓰기) |
| 9056 | MT와 PLC통신이 안될 때, Touch 기능의 여부. | ON일 때 Touch 안됨, OFF일 때 Touch 가능 (읽기/쓰기) |

| 9060 ~9061 | Keypad Control Bit, Keypad를 화면 왼쪽에 호출시 사용 | 화면을 Touch하여, 숫자를 입력 하거나 ASCII입력할 때, 왼쪽 터치시 bit가 On. Keypad의 Enter, ESC Key에 의해 bit가 OFF됨. Direct Window로 활용 (읽기) |
| --- | --- | --- |
| 9062 | Keypad를 왼쪽 위에 호출시 사용 | 왼쪽 터치 시 ON (읽기) |
| 9063 | Keypad를 왼쪽 아래에 호출시 사용 | 왼쪽 아래 터치 시, ON (읽기) |
| 9064~9065 | Keypad를 오른쪽에 호출시 사용 | 오른쪽 터치 시, ON (읽기) |
| 9066 | Keypad를 오른쪽 위에 호출시 사용 | 오른쪽 위 터치 시, ON (읽기) |
| 9067 | Keypad를 오른쪽아래에 호출시 사용 | 오른쪽 아래 터치 시, ON (읽기) |
| 9068~9069 | Keypad를 전 영역에 호출 시 사용 | 전구역 터치 시, ON (읽기) |
| 9080 | Keypad를 중앙 위쪽에 호출시 사용. | 중앙 위쪽 터치 시, ON (읽기) |
| 9081 | Keypad를 중앙 아래에 호출시 사용. | 중앙 아래 터치 시, ON (읽기) |
| 9090 | Event log 삭제 | Event log 삭제기능.ON후 자동 OFF됨. |

Keypad control bit position:

Left and Top:

LB9062

Right and Top:

LB9066

Left:

LB9060, B9061

All side:

LB9068, LB9069

Right:

LB9064, LB9065

Left and Bottom:

LB9063

Top:

LB9080

Bottom:

LB9081

Left and Bottom:

LB9067

2 Local Word (LW)

LW0000 ~ LW8999 (사용자용)	LW9000 ~ (시스템용)

| 위 치 | 설 명 | 비 고 |
| --- | --- | --- |
| 9000 | Recipe Word (RWI) 인덱스표시 | RW(Recipe Word) 와 RB(Recipe Bit)를 액세스하여 색인기능사용. |
| 9002 ~ 9003 | 수치 입력의 최대치 (수치 입력일 때) | (1)수치 입력 시 최대치가 표시됨, 입력 후 0이 표시됨. (최대치 9002~9003까지 2Word 사용 가능) (읽기) |
| 9004 ~ 9005 | 수치 입력의 최소치 (수치 입력일 때) | (1) 수치 입력 시 최소치가 표시됨, 입력 후 0이 표시됨.(최대치 9002~9003까지 2Word 사용 가능) (읽기) |
| 9006 | Message Board 도구 상태 | 0:펜으로 쓰기, 1:지우개, 2:드래그하여 지우기 (읽기) |
| 9007 | 펜 굵기 표시 | Message Board 사용 시 Pan의 굵기를 표시 0: 1Pixel 1: 2Pixel 2: 3Pixel (읽기) |
| 9008 | 펜 색상 표시 | 256색상 중 현재 선택되어 있는 Pen의 색상을 표시(0~255) (읽기) |
| 9010 | 시계Data(초) | PLC시간변환, BCD양식, (0 ~ 59) (읽기/쓰기) |
| 9011 | 시계Data(분) | PLC시간변환, BCD양식, (0 ~ 59) (읽기/쓰기) |
| 9012 | 시계Data(시 | PLC시간변환, BCD양식, (0 ~ 23) (읽기/쓰기) |
| 9013 | 시계Data(일) | PLC시간변환, BCD양식, (0 ~ 31) (읽기/쓰기) |
| 9014 | 시계Data(월) | PLC시간변환, BCD양식, (0 ~ 11) (읽기/쓰기) |
| 9015 | 시계Data(년) | PLC시간변환, BCD양식, (0 ~9999)(읽기/쓰기) |
| 9016 | 시계Data(요일) | PLC시간변환, BCD양식, (0 ~ 6) (읽기/쓰기) |
| 9020 | 사용 아이템 개수. |  |
| 9034~ 9035 | MT사용 시간 | 전원ON시부터 OFF시까지 카운터 됨 0.1초단위 (읽기/쓰기) |
| 9040 ~9041 | Password | 비밀번호, 32Bit 수치 (단지 9자리 숫자로 한정) (쓰기) |
| 9042 | 비밀번호의 등급 | (읽기) |
| 9043 | 보호등급을 설정 | 강제 설정함 (쓰기) |
| 9044 | Touch process mode | (읽기/쓰기) |
| 9050 | 현재화면(Window) 번호를 표시. | Register를 이용하여 Slave와 Master의 화면을 서로 일치시킵니다. (읽기) |
| 9051 | 전환 화면 번호표시 | PLC로 화면(Window)전환 된 결과를 표시합니다. (읽기/쓰기) |

| 9054 | Report printout , 프린터 양식 설정 | 0 : Text & Meter & Trend 1: 0 & Shape but no pattern 2: 0 & Bitmap 3: 2 & Shape but no pattern 4: All (Read / Write) |
| --- | --- | --- |
| 9055 | Offset 설정. | PLC Control의 창 전환 & 화면 프린트 시, 옵셋설정 (읽기/쓰기) 예) PLC Control ( D0 ) 에 화면 전환시 , LW9055= 1, 그리고 D0 = 10 이면, MT 화면을 11(1+10=11)번 화면 으로 전환. 11번 화면으로 전환 후, ( D11=10 ) |
| 9057 | 알람 이력 아이템 사이즈 | 모든 아이템 사이즈의 작업 정보 (읽기) |
| 9058-9059 | 알람 이력 사이즈 | 작업 정보 데이터베이스 ( 전체 아이템*아이템 사이즈+작업정보사이즈 ) 사이즈 (read only) |
| 9060 ~ 9075 | Numeric Input 과 ASCII Input 의 현재 입력치 | 수치입력 또는 문자입력의 입력치를 나타냄. 예)수치입력/문자입력: ASCII Data를 사용하여 2자리=LW9075 (1Word), 4자리=LW9074 (2Word),…… 12자리=LW9070 (6Word)설정, (읽기) |
| 9080 ~ 9085 | File 이름 | ASCII Data로 File이름을 나타냄, 모두12bytes (읽기) |
| 9086 ~ 9087 | File 용량 | Numeric Data로 File용량을 나타냄. 단위는 bytes로 표시 (읽기) |
| 9088 ~ 9089 | File 용량 | Numeric Data로 File용량을 나타냄. 단위는 Kbytes로 표시 (읽기) |
| 9090 ~9091 | Compile한 프로그램 원본. | Numeric Data로 이 프로그램의 Compile Version ID를 표시 (읽기) |
| 9092 | Compile한 프로그램의 일시(년) | Numeric Data로 이 프로그램의 Compile 일시 (년)를 표시 (읽기) |
| 9093 | Compile한 프로그램의 일시(월) | Numeric Data로 이 프로그램의 Compile일시 (월)를 표시 (읽기) |
| 9094 | Compile한 프로그램의 일시(일) | Numeric Data로 이 프로그램의 Compile일시 (일)를 표시 (읽기) |
| 9100 9101 | Indirect Addressing 이며 PLC외부용으로 사용 | 9100 Indirect Window를 지정. 9101 Indirect Offset을 지정 |
| 9130 | 언어변환 | 언어 0-3(읽기/쓰기) 예) 0일 때 한글,1일 때 영어, 2일 때 중국어, 3일 때 일본어 |

3 Reserved Recipe Word

Recipe memory, 모두 128Kbyte Words

RW00000 ~ RW59999(사용자용)	RW60000 ~ (시스템용)

| 위 치 | 서 술 | 비 고 |
| --- | --- | --- |
| 60000 | 시계Data(초) | BCD 양식, 내부DATA ( 0 ~ 59) (읽기/쓰기) |
| 60001 | 시계Data(분) | BCD 양식, 내부DATA ( 0 ~ 59) (읽기/쓰기) |
| 60002 | 시계Data(시) | BCD 양식, 내부DATA ( 0 ~ 23) (읽기/쓰기) |
| 60003 | 시계Data(일) | BCD 양식, 내부DATA ( 0 ~ 31) (읽기/쓰기) |
| 60004 | 시계Data(월) | BCD 양식, 내부DATA ( 0 ~ 11) (읽기/쓰기) |
| 60005 | 시계Data(년) | BCD 양식, 내부DATA ( 0 ~ 9999) (읽기/쓰기) |
| 60006 | 시계Data(주기) | BCD 양식, 내부DATA ( 0 ~ 6) (읽기/쓰기) |
| 시계Data 주의 사항: Numeric Data로 시계Data의 시간이 나타나고, 그 수치를 Numeric Input으로 고칠 수 있으나 쓸 때 주의하여야 함. 예를 들어, RW60000(초) 범위는 0 ~59이다. 60이상의 수치를 설정하면 RW60000(초)는 계속하여 증가 되므로 주의 해야 함. |  |  |

4. Recipe Bit (RB)

Recipe Memory 앞에서 소개한 Recipe Word (RW)와  대응되어 사용합니다.

RB0000 ~ RB2047F (사용자용)

RB100  RW10의 1번째 Bit (하나의  Word는 16개의 Bit)

RB1008  RW100의 9번째 Bit 	RB1020A  RW1020의 11번째 Bit

RB2047F  RW2047의 16번째 Bit

| 1 WORD |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| F | E | D | C | B | A | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 |
| BIT16 | BIT15 | BIT14 | BIT13 | BIT12 | BIT11 | BIT10 | BIT9 | BIT8 | BIT7 | BIT6 | BIT5 | BIT4 | BIT3 | BIT2 | BIT1 |

5.RWI. RBI

Recipe Memory

LW9000과 함께 사용합니다.

RWI0000 ~ RWI32767(사용자용)

RBI0000 ~ RBI 2047F(사용자용)

RWI  RW가 Recipe Memory 의 Index Register

RBI  RB 가 Recipe Memory 의 Index Register

RWI. RBI 는 LW9000과 함께 사용합니다.

예 : ASCII Data

Read address = RWI 200

LW90000 = 50이라면 ASCII Data는 RW250의 수치가 나타납니다.

LW90000 = 36이라면 ASCII Data는 RW236의 수치가 나타납니다.

6. Ms_ RB. Ms_LB. Ms_RW. Ms_LW

이상의 4가지로 MT가 여러 대로 Link(1:N) 통신 할 때 사용합니다.

MT 여러 대를 Link(1:N) 통신 할 때, 효과적으로 Data를 전달 할 수 있습니다.

예를 들어, 일반적인Trend Display 표현 시  Slave가 Master를 통하여,  PLC의 Data를 읽어오기 때문에 속도가 느립니다.

이때, Master가 Read한  PLC의 Data를 Ms_ RB. Ms_LB. Ms_RW. Ms_LW등으로 공유하면 보다 빠른 속도로 Data를 처리 할 수 있습니다.

Ms_ RB: Master 내부의 Register(RB) 를 Read합니다. 범위는 0000 ~ 4095입니다.

Ms_ RB 100  Master 내부 LW10은 1 Bit를 Read합니다

Ms_ RB 1008  Master 내부 LW100은 9 Bit를 Read합니다

Ms_ RB 1000A  Master 내부 LW1000은 11 Bit를 Read합니다

Ms_ RB 4090F  Master 내부 LW4090은 16 Bit를 Read합니다

Ms_ LB: Master 내부의 Register(LB) 를 Read합니다. 범위는 0000 ~ 9999입니다.

Ms_ LB 100  Master 내부 LB 100을 Read합니다

Ms_ LB 3200  Master 내부 LB 3200을 Read합니다

Ms_ RW: Master 내부의 Register(RW) 를 Read합니다. 범위는 0000 ~ 65535입니다.

Ms_ RW 11100  Master 내부 RW 11100을 Read합니다

Ms_ RW 32001  Master 내부 RW 32001을 Read합니다

Ms_LW: Master 내부의 Register(LW) 를 Read합니다. 범위는 0000 ~ 9999입니다.

Ms_ LW 1100  Master 내부 LW 1100을 Read합니다

Ms_ LW 2001  Master 내부 LW2001을 Read합니다

PS : 일반적으로 MS-LW.  Ms_LB.  Ms_RW.  Ms_LW의 4가지 Device는 Slave에서 사용합니다.

작화 할 때 4가지의 MT Device을 설정한 후, MT가 동작할 때 Slave는 자동적으로 MT내부의 Register를 Read합니다. 단 Master가 편집화면이라도 이 접점을 사용하면 Master가 작동할 때 자동적으로 MT내부에 대응하는 Register를 찾습니다.